MAHARASHTRA JEEVAN PRADHIKARAN

MARATHWADA WATER GRID

PDR FOR BEED DISTRICT

ESTIMATED COST :- RS. 4801.86 CR.

YEAR 2019-20

Index

| Chapter |  |  | Particulars | Page. No. |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  |  | From | To |
| 1 |  |  | Report – Beed District WSS |  |  |
|  | 1 |  | General Information |  |  |
|  |  | 1.1 | Population of Beed District |  |  |
|  |  | 1.2 | Rainfall History of Beed District |  |  |
| 2 |  |  | Hydraulic Design |  |  |
| 3 |  |  | Bill of Quantities (BOQ’s) |  |  |
| 4 |  |  | Technical Specifications |  |  |
| 5 |  |  | Drawings |  |  |

CHAPTER : I

REPORT – BEED DISTRICT WSS

- EXEC.MAHARASHTRA JEEVAN PRADHIKARAN

MARATHWADA WATER GRID

PDR FOR BEED DISTRICT

- GENERAL INFORMATION

1

HE	Beed Districtissituated in the centre of the Aurangabad division of the state between 180 27' and 19027' north latitude and 740 49' and 760 44' east longitude. It has an area of 10,921.8 square kilometres and a population of 2917049. The east – west extension of Beed district is nearly 268 km and north – south distance of the district is 127 kms. The westward part of the Ashti tahsil of the district that projects into the Ahmadnagar district, the shape of the district is broadly that of a trapezium. The northern and the southern sides of which are nearly parallel. It is bounded by Aurangabad and Parbhani districts on the north, Parbhani and Osmanabad districts on the east, Osmanabad district on the south and Ahmadnagar district on the west.

The district derives its name from that of its headquarters town of Bhir,for the origin of which two explanations are given. The town is set in a hollow or a Beel into the scarp of the Balaghat plateau trenched by the Bindsura river, and hence the name of Bhir, the term Beed having undergone this transformation in course of time. As, such a piedmont location provides an abundance of sub-terranean water supplies tapped by unfailing wells, the Persian word Bhir meaning water might also explain the origin of the name.

  - Population of Beed District:

The details of the population of urban and rural  areas as under: —

| Sr.No. | Taluka | Urban /Rural | Present Population |
| --- | --- | --- | --- |
| 1 | Beed | Urban | 1,65,310 |
|  |  | Rural | 3,92,611 |
| 2 | Georai | Urban | 39,394 |
|  |  | Rural | 3,53,269 |
| 3 | Shirur | Urban | 6,822 |
|  |  | Rural | 1,39,216 |
| 4 | Patoda | Urban | 16,697 |
|  |  | Rural | 1,16,622 |
| 5 | Ashti | Urban | 13,446 |
|  |  | Rural | 2,60,689 |
| 6 | Ambajogai | Urban | 82,946 |
|  |  | Rural | 2,07,145 |
| 7 | Majalgaon | Urban | 57,712 |
|  |  | Rural | 2,18,511 |
| 8 | Kaij | Urban | 37,512 |
|  |  | Rural | 2,33,083 |
| 9 | Dharur | Urban | 22,667 |
|  |  | Rural | 1,16,509 |
| 10 | Wadwani | Urban | 15,012 |
|  |  | Rural | 87,072 |
| 11 | Parli | Urban | 1,05,249 |
|  |  | Rural | 2,29,555 |
|  | Total | Urban (11) | 5,62,767 |
|  |  | Rural (11) | 23,54,282 |
|  | Grand Total (U + R) |  | 29,17,049 |

1.2 Rainfall History of Beed District:

Beed District facing acute shortage of drinking water since many years. The average expected rainfall of Beed Dist.is 666.36 mm.&rainfall report of Beed dist. from 1991 to 2018 is as follows:

| Year | June to October |  |  |
| --- | --- | --- | --- |
|  | Actual | Average | Percentage |
| 1991 | 328.2 | 664.6 | 49.38% |
| 1992 | 689.8 | 664.6 | 103.79% |
| 1993 | 647 | 664.6 | 97.35% |
| 1994 | 375.6 | 664.6 | 56.52% |
| 1995 | 652.8 | 664.6 | 98.22% |
| 1996 | 937.4 | 664.6 | 141.05% |
| 1997 | 482.6 | 664.6 | 72.62% |
| 1998 | 1143.1 | 664.6 | 172.00% |
| 1999 | 504.2 | 664.6 | 75.87% |
| 2000 | 886.8 | 664.6 | 133.43% |
| 2001 | 734.2 | 663.1 | 110.72% |
| 2002 | 582.8 | 663.1 | 87.89% |
| 2003 | 459.6 | 663.1 | 69.31% |
| 2004 | 542.8 | 663.1 | 81.86% |
| 2005 | 867.6 | 663.1 | 130.84% |
| 2006 | 615.8 | 663.1 | 92.87% |
| 2007 | 662.2 | 663.1 | 99.86% |
| 2008 | 696 | 663.1 | 104.96% |
| 2009 | 677 | 663.1 | 102.10% |
| 2010 | 793 | 663.1 | 119.59% |
| 2011 | 961 | 663.1 | 144.93% |
| 2012 | 440.7 | 666.36 | 66.14% |
| 2013 | 671.4 | 666.36 | 100.76% |
| 2014 | 370.5 | 666.36 | 55.60% |
| 2015 | 330.4 | 666.36 | 49.58% |
| 2016 | 835 | 666.36 | 125.31% |
| 2018 | 334.7 | 666.36 | 50.23% |

Rains are scarce and occur only during the Monsoon from mid-June to September. Annual average rainfall is 66.6 cm (26.22 inches). The average rain fall has dropped 9.6 cm from the averages recorded during the 1900s Average number of rainy days in a year are 41 only. September gets the maximum rainfall in a year while July has the maximum rainy days. Highest rainfall recorded in 24

hours (19.18 cm) occurred on 17 August 1887. . Beed receives low rainfall because it is located in rain shadow area.From the above data it is seen that day by day percentage of  rainfall decreasing gradually and available water cannot cater the basic demands of citizens of district.  Every year after monsoon season water is supplied by deploying tankers and government has to spend lot of money over it.

To overcome this difficulties permanent solution on deficiencies of water is required. For this purpose Govt. of Maharashtra has proposed loop system of water network connecting many dams of Marathwada region known as Marathwada Grid.

#### 2.Technical Summary of  Beed District PDR

#### 2.1 PipeInfrastructure

The total pipe length included in this  Beed  district PDR is around 1078 Km. Out of this some 373  Km of pipe are categorized as BWS and mainly will convey raw water. Among this segment of the system, the biggest pipe of all diameters will be included –this is a segment of 2500 mm in Diameter from the Jayakwadi intake to the splitting of the pipe. The SWS portion of the system includes some 705 Km of potable water pipe. This segment of the pipes contain Diameter range from 2500 mm MS pipes down to  200 mm DI pipes.

2.2 Main pumping stations in theregion:

Five PS are for potable water at the downstream of the WTP's. It has been decided that since the WTP's serves not only the local location attached to the facilities, but some locations in remote areas, the delivery potable water pump will be attached to the WTP's not in separate yard.

#### WTP's:

#### Following WTP's are proposed in the scheme.

| 1 | Beed (Gadhi) - 112 MLD |
| --- | --- |
| 2 | Majalgaon - 20 MLD |
| 3 | Ambajogai - 35 MLD |
| 4 | Kaij-Dharur - 35 MLD |
| 5 | Ashti-Patoda-Shirur -53 MLD |

#### Details of Pumping Stations are as follows:

| Sr. No. | Description | Discharge in m3/hr | Head in m | HP/Pump | No. of Working Pumps | No. of Standby Pumps | Total No. of Pumps |
| --- | --- | --- | --- | --- | --- | --- | --- |
| A | Raw Water Pumping Stations |  |  |  |  |  |  |
| 1 | Pump to Beed | 2944.48 | 30 | 495 | 3 | 2 | 5 |
| 2 | Booster to manjara Pump | 3138.12 | 156 | 2681 | 9 | 3 | 12 |
| B | Pure Water Pumping Stations |  |  |  |  |  |  |
| 1 | Pump to Ashti | 498.79 | 249 | 683 | 4 | 2 | 6 |
| 2 | Ambajogai-B-1Pump | 385.61 | 45 | 100 | 3 | 2 | 5 |
| 3 | Georai WTP Pump | 1015.08 | 150 | 885 | 5 | 2 | 7 |
| 4 | Majalgaon WTP Pump | 750.97 | 86 | 375 | 3 | 2 | 5 |
| 5 | Beed R-2 Pump | 464.83 | 150 | 442 | 3 | 2 | 5 |
| C | Inline Booster Pumping Stations |  |  |  |  |  |  |
|  | 40 HP VT Pumps (6+2) - 8 Nos |  |  |  |  |  |  |

#### 2.3 The hydraulic level of service and the transmissioncapacity

Preparation of the WSS for the Beed districts were done using Indian local standards.Main hydraulic norms use for the creation of the PDR stage plan are listed as below.

Water supply schemes design level

| Service Aspect | Guideline |
| --- | --- |
| Hours of service | Continuous – 24 hours per day |
| Hours of supply | All BWS and trunk lines are calculated for 20h/day operation |
| Water quality | Water supplied should comply with Indian standards IS 10500 – 2012 guidelines for drinking water. Deviations may be made where the standards are difficult to achieve, provided such deviations are not injurious to health and provided consumers are notified of necessary precautions to be taken. |
| Reliability | To provide service to all consumers 24/7 supply by enhancing water from raw water resources to WTP's and furthered to GSR/ESR tank to enable continuous supply to the end consumer level. |
| Metering | All production, treatment and consumers should have metered supply. |
| Pressure | Not less than 15m residual pressure at any point in the grid. Any pressure of above 100mH2O in trunk line must be regulated before delivery to secondary users |
| Hydraulics | Gradients for flow less than 5.0m/Km or not more than 2.0-2.2m/sec. |
| Tertiary WSS | All local water supply schemes that will be connected to the SWS and does not appear in the WSMP nor in the PDR. |
| Pipe pressure grade | K9 for DI pipes, 64ATM for MS pipes, 10bars for HDPE pipes |

The Water Resources for the scheme (quantities)

  - Jaykawadi Dam is the main water resources for the proposed WSS. Final location of Beed district WSS will be clarified in consultation with the Irrigation Department. Major intakes from Jaykawadi Dam with 2050 capacity.

#### Water quality consideration of the WSS

#### (requirements, standards and facilities)

In order to assure water quality level of the entire potable water system, the Beed WSS suggested the construction of several WTP's or extension of current ones as listed here in Table. Where parameters for the quality of water doesn't appear in the Indian standards, WHO figures should be adopted.

The water quality minimum level to be provided by WTP's.

| Substance | Unit | Maximum Acceptable Concentration | Maximum Allowable Concentration | Treated Water Standard as per IS 10500 - 2012 |
| --- | --- | --- | --- | --- |
| Total solids |  | 500 | 1,500 | – |
| Colour |  | 5 units | 50 units | 5 Max |
| Turbidity | NTU | 5 units | 25 units | 5 Max |
| Taste | NA | Un objectionable | – | – |
| Odour | NA | Un objectionable | – | Agreeable |
| Iron | ppm | 0.3 | 1 | 0.3 Max |
| Manganese | ppm | 0.1 | 0.5 | – |
| Copper (Co) | ppm | 1 | 1.5 | – |
| Zinc (Zn) | ppm | 5 | 15 | – |
| Calcium (Cu) | ppm | 75 | 200 | – |
| Magnesium (Mg) | ppm | 50 | 150 | – |
| Sulphate (SO4) | ppm | 200 | 400 | – |
| Chloride (Cl) | ppm | 200 | 600 | 250Max |
| pH range | Unit | 7.0–8.5 | 6.5–9.2 | 6.5 - 8.5 |
| Magnesium & sodium sulphate |  | 500 | 1,000 | – |
| Phenolic substances (as phenol) | ppm | 0.001 | 0.002 | – |
| Carbon chloroform extract (CCE) (from organic pollutants) | ppm | 0.2 | 0.5 | – |
| Alkyl benzyl sulfonate |  | 0.5 | 1 | – |
| Nitrates | ppm | – | – | 45 Max |
| Residual free Chlorine | ppm | – | – | 0.2 Min |
| Fluoride | ppm | – | – | 1Max |
| Total hardness |  | – | – | 200Max |

#### Description of the WSS's ( Topology. Water supply pattern )

Unlike other water supply scheme with in Marathwada, the Beed districts water supply will be fully rely on pumping raw water from the Jayakwadi Dam. Most of the surface area in the region has an elevation above the Jayakwadi water dam thus in general two levels of pumping will be required for this region:

#### Physical pipe inventory for proposed WSS's (Both RW + PWquality)

| Type &Dia of pipe | Length in KM. |
| --- | --- |
| Ductile Iron |  |
| 1000 | 136.90 |
| 900 | 19.27 |
| 800 | 132.40 |
| 700 | 59.52 |
| 600 | 110.18 |
| 500 | 34.28 |
| 400 | 207.77 |
| 350 | 11.36 |
| 300 | 71.72 |
| 200 | 1.44 |
| TOTAL DI | 796.58 |
| MS |  |
| 2500 | 118.51 |
| 2200 | 67.74 |
| 2000 | 22.93 |
| 1500 | 10.05 |
| 1250 | 27.12 |
| 1200 | 35.67 |
| Total MS | 282.03 |
| Grand Total (DI+MS) | 1078.61 |

Hydraulics design criteria's

Transmission mains will be designed to have minimum hydraulics lopes of 0.3% for DN≤ 200 mm and 0.2% for DN >200 mm. % is 10m/Km slope.

Flow velocities in transmission mains will be between 0.6 m/s and 2.2 m/s, and will be lower in smaller diameter pipes and higher in larger diameter pipes. The maximum operating velocity will be 2.2m/s to ensure safe operation of the pipeline.

Transmission mains will be designed using the Hazen-Williams formula for pipeline head losses. Given that the pipelines will have to perform according to the required ultimate demand for planning years, the following C factors are recommended to be used for this project.

- Steel or ductile iron (DI) pipe materials:	C=140

- Dia meters bigger than 1,500mm of any material:	C=140

- Dia meters bigger than 2,000mm of any material:	C=140

Working pressure will be limited to 70% of the test pressure of the pipe. The Residual pressure will be maintained at minimum of 10m, except for sections downstream of break-pressure tanks.

#### Pumps design criteria's

The following list will be a guide line for the detailed planning of pumping units and pumping sets.

- Minimum pump efficiency 80% per each unit.

- At least 20% of the pumps in the pumping array (1 out of 5, 2 out of 10) will be equipped with variable frequency drive

- The manifold will be sized with two diameters larger than the impeller's diameter. Valves and non-return valves one diameter more than pump impellers.

- All pumping stations will be built and equipped with a minimum of a two meter distance between electricmotors

- All civil engineering work will be done in a way that it will be possible to accommodate all pumps as for the2050

- The required capacity of standby pumps will be calculated using the following equation: % standby capacity > (1 / total no. of dutypumps)

- It is recommended that pumps and impellers be installed vertically in dry installations (also called surfaceinstallation).

- Only in the case of pumping more than 150-160 meter TDH head and electric motors bigger than 850 Kw, it will be allowed to consider two attached pumps in inline configuration. That will allow resize of theelectric motorsize.

- Surge preventing systems with both surge tanks and surge anticipating valves will be a mandatory in each pump stations of any size and any TDH. Surge analyses will be calculated according to the standards for the said in India including detailed calculation for the size of tanks, size and number of the valves and the filling ration of the tank with pressurized air.

#### Other components design criteria

Section valves (symbolized "SV") will be installed for facilitating maintenance of the system:

- Maximum 10 km distance between devices

- Critical points Air valves (symbolized AV) will be installed:

- Maximum 0.7 km distance between devices

- High topographical points

- Severe change and critical points in hydraulic gradient Washout valves (symbolized "WV") will be installed at low points and sized to ensure drainage of the pipe sections.

- Surge protection valves (symbolized "SPV") and cathodic protection equipment will be designed and installed according to detailed analysis by suitable experts.

#### Water quality monitoring criteria's

Existing regional water laboratories are sufficient for periodic monitoring of borehole waters but each surface water treatment plant should have its own facility for monitoring the quality of both the raw water and the processed water at different stages of treatment. Well-equipped chemical laboratories will be provided for the large treatment plants and appropriate test kits will be provided for the smaller treatment plants.

The following methods of water treatment are considered to be suitable, used in different combinations as necessary to achieve the desired results:

- Screening or straining

- Roughing or pretreatment filters

- Primary sedimentation

- Chemical coagulation, flocculation and secondary settling

- Filtration either by slow sand or rapid gravity filtration

- Disinfection

- Control of algae

- Taste and odor control

- Softening

- Removal of iron and manganese

- De-fluoridation ofwater

Minimum treatment will be disinfection for groundwater sources and some form of filtration followed by disinfection for surface water sources. The most feasible option (technically and financially) will be developed for each town/source individually

- Hydraulic Criteria for Pumping Stations

The following list presents the design criteria for pumps and boosters for the level of preliminary design report. Given that the pipes will have to perform according to the required ultimate demand for planning years, the following criteria recommended to be used for this project:

  - Minimum pump efficiency 80%

  - The manifold will be sized with one diameter larger than the impeller's diameter.

  - All pumping stations will be built and equipped with a minimum of a two pump array (distance >4m)

  - The required capacity of standby pumps will be calculated using the following equation: % standby capacity = (1 / total no. of duty pumps)

  - It is recommended that pumps and impellers be installed vertically in dry installations (also called surfaceinstallation).

  - Number of stands by pump will not be less than 1 Stand by motor per 3 workingmotors

##### Pumping house design criteria:

  - Minimum net height of house – 5meters

  - Minimum space between pumping units – 4meters

  - All houses will include staff room, electric room, control room, highvoltage room

  - Free passage in the building for load/unload heave equipment – 5meters

  - Crane for lifting heavy loads – up to 2ton

##### Electric consideration criteria:

  - Electric motor power – units of 350 Kw and 500KW

  - Soft starters for Pumps will be mandatory

  - At least two pumps units will be equipped with variable frequency drive

  - All grid connection will be high voltage grid

  - Each site will include electric transformation unit to low voltage supply

  - Electric room will be separate for high and low voltage

  - Local SCADA (System Control and Data acquisition) system for each pump array, will be part of the final drawing of the Pumping Stations.

##### Miscellaneous

  - All pumping stations will include surge preventing system. Calculation of the required size/No of valve by the contractor.

  - All pumping stations will include surge preventing tank. Calculation of the required size/No of valve by the contractor.

  - All accessories like air valves (static and kinetics), PRV valve if required, score valves, water meter, manifold accessories, pressure and flow gauges will be part of the final drawing of thePS.

  - Water hammer preliminary analyses will be done at the stage of finalizing the pumps array, the TDH as a result of the pumps curve

Cost summary of all Capex of the BEED WSS, exclude intakes

| No | WSS Name | Total Cost (Cr. INR) |
| --- | --- | --- |
| 1 | Beed WSS | 4801.86 |

#### ECURRENT PDR

CHAPTER : II

HYDRAULIC DESIGNS

CHAPTER : III

BILL OF QUANTITIES (BOQ’S)

TECHNICAL SPECIFICATIONS

CONTENTS

| A. | TRANSMISSION LINE | 3 |
| --- | --- | --- |
| 1. | MATERIAL FOR CONSTRUCTION | 3 |
| 2. | EARTHWORK | 11 |
| 3. | FILLING | 13 |
| 4. | CONCRETE WORK | 14 |
| 5. | PLASTER WORK | 18 |
| 6. | FINISHES | 21 |
| 7. | PREPARATION OF SURFACES | 23 |
| 8. | STEEL WORK | 29 |
| 9. | ELECTRIFICATION | 32 |
| B. | PROJECT SPECIFICATION | 40 |
| 1. | PIPE | 40 |
| 2. | VALVES | 60 |
| C. | PUMPS SPECIFICATIONS | 81 |
| 1. | VERTICAL TURBINE PUMP (WATER LUBRICATED) ESSENTIAL DESIGN | 81 |
| 2. | CENTRIFUGAL PUMP (PURE WATER) ESSENTIAL DESIGN | 89 |
| 3. | HORIZONTAL CENTRIFUGAL PUMPS | 90 |

# A. TRANSMISSION LINE

- Material for Construction

  - WATER

Water shall not be salty of brackish and shall be clean, reasonably clear and free from objectionable  quantities  of  silt  and  trace  of  oil  and  injurious  alkalis,  salts,  organic matter and other deleterious material which will either weaken the mortar of concrete of cause efflorescence of attack the steel in RCC Container for transport, storage and handling of water shall be clean, water shall conform to the standards specified in I.S. 456-2000.

If  required  by  Engineer-in-charge, it  shall  be  tested  by  comparison with  distilled water. Comparison shall be made by means of standard cement tests for soundness, time of  setting and mortar strength as specified in I.S. 269-1979. Any indication of unsoundness, change in time of setting be 30 minutes or more of decrease of more than 10 per cent in strength of mortar prepared with water sample when compared with the results obtained with mortar prepared with distilled water shall be sufficient cause for rejection of water under test.

Water for curing mortar, concrete of masonry should not be too alkaline. It shall be free of elements that significantly affect the hydration  reaction  of  otherwise interfere with the hardening of concrete during curing of those which produce objectionable stains of other unsightly deposits on concrete of mortar surfaces. Hard and bitter water shall not be used for curing Potable water will be generally found suitable for curing mortar of concrete.

  - LIME

Lime shall be hydraulic lime as per I.S. 712-1973. Necessary test shall be carried out as per I.S. 6932 (Parts  X), 1973. The following field tests for lime are to be carried out:

- A very rough idea can be formed about the type of lime by its visual examination

i.e. At lime bears pure white colour lime in form of porous lumps of dirty while colour indicates quick lime, and solid lumps are the un-burnt lime stone.

- Acid tests  for  determining  the  carbonate  content  in  lime,  excessive  amount  of impurities and rough determination of class of lime.

Storage shall comply with I.S. 721-1973. The slaked lime, if stored, shall be kept in a weather  proof  and  damp-proof  shed  with  impervious floor  and  sides  to  protect  it against rain, moisture, weather and extraneous materials mixing with it. All time that has been damaged in any way shall be rejected materials shall be removed from site of   work.   Field-testing  shall  be   done  according  to   I.S.   1624-1974  to   show  the acceptability of materials.

  - CEMENT

Cement shall be 53 Grade Ordinary Portland cement as per I.S. 12269-1976 and 43 Grade Ordinary Portland cement as per I.S. 8112-1976.

## White Cement

The white cement shall confirm to IS-80412 E 1978

## Coloured cement

Coloured cement shall be with white of grey Portland cement as specified in the item of the work. The pigments used for coloured cement shall be of approved quality and shall not exceed 10 % of cement used in the Mix. The mixture of pigment shall be properly grounded to have a uniform colour and shade. The pigments shall have such properties to provide for durability under exposure to sunlight and weather.

The pigment shall have the property such that it is neither affected by the cement nor detrimental to it.

  - SAND

Sand shall be natural sand, clean, well graded, hard strong durable and gritty particle free from injurious amounts of dust clay, kankar nodules, soft of flaky particles, shale, alkali, salts organic matter, loam, mica of other deleterious substances and shall be got approved from the Engineer-in-charge. The sand shall not contain more than 8 percent of silt as determined by field test. If necessary the sand shall be washed to make it clean.

## Course sand

The  fineness modules of  coarse sand  shall  not  be  less  than  2.5  and  shall  not exceed 3.0. The sieve analysis of coarse shall be as under:

| I.S. Sieve Designation | Percentage by weight passing Sieve | I.S. Sieve Designation | Percentage by weight passing sieve |
| --- | --- | --- | --- |
| 4.75 mm | 100 | 600 micron | 30-100 |
| 2.36 mm | 90-100 | 300 micron | May-70 |
| 1.18 mm | 70-100 | 150 micron | 0-50 |

The crushing strength of grit will be such as to allow the concrete in which it is used to build up the specified strength of concrete. The necessary test for grit shall carried out as per the requirement of I.S. 2386 (Parts I to VII) 1963 as per instructions of the Engineer-in-charge. The necessity of test

## Fine sand

The fineness modulus shall not exceed 1.0. The sieve analysis of fine sand shall be as under:

| I.S. Sieve Designation | Percentage by weight passing Sieve | I.S. Sieve Designation | Percentage by weight passing |
| --- | --- | --- | --- |
| 4.75 mm | 10 | 600 micron | 40-85 |
| 2.36 mm | 100 | 300 micron | May-50 |
| 1.18 mm | 70-100 | 150 micron | 0-10 |

  - AGGREGATE

Grit  shall  consist  of  crushed, of  broken stone and  be  hard  strong, dense, durable, clean, of proper graduation and free from skin of coating likely to prevent adhesion of mortar Grit shall generally by cubical in shape and as far as possible flaky elongated pieces shall be avoided. It shall generally comply with the provisions of I.S. 383-1970. Unless special stone of particular quarries is mentioned, grit shall be obtained from the best black trap or equivalent hard stone as approved by the Engineer-in-charge. The grit shall have no deleterious reaction with cement.

| I.S. Sieve Designation | Percentage by weight passing Sieve | I.S. Sieve Designation | Percentage by weight passing sieve |
| --- | --- | --- | --- |
| 12.50 mm | 100 | 4.75 micron | 0-20 |
| 10.00 mm | 85-100 | 2.36 micron | 0-25 |

Will be decided by the engineer-in-charge. Cinder aggregates shall be well burnt furnace residue obtained from furnace using call fuel only. It shall be sound clean free form clay, dirt, ash of other deleterious matter.

The average grading for cinder aggregates shall be mentioned below.

## Stone grit

Proportion of Mix: Mortar shall consist of such proportion of slaked lime and sand as may be specified in the item. The asked lime and sand be measured by volume.

Proportion of Mortar: Lime mortar shall be prepared by wet process as per I.S. 1625- 1971 power driven the 180 revolutions with sufficient water. Water shall be added as required during grinding (care being taken not to add more water) that will bring the mixed material to a consistency of stiff paste. Thoroughly wetted sand shall then be added evenly and the mixture ground for another 180 revolutions.

Storage: Mortar shall always be kept damp, protected from sun and rain till used up, covering it by tarpaulin of open sheds.

Use: All mortar shall be used as soon as possible after grinding. It should be used on the day on which it is prepared. In no case mortar made earlier than 36 hours shall be permitted for use.

## Cement Mortar

Proportion of  Mix:  Cement  and  sand  shall  be  mixed  to  specified proportion, sand being measured by measuring boxes. The proportion of cement will be by volume on the basis of 50 kg/Bag of cement being equal to 0.0342 m3. The mortar may be hand mixed of machine mixed as directed.

Preparation of Mortar: In hand mixed mortar cement and sand in the specified proportions shall be thoroughly mixed dry on a clean impervious platform by turning

over at least 3 times of more till a homogenous mixture of uniform colour is obtained. Mixing platform shall be so arranged that no deleterious extraneous material shall get mixed with mortar of mortar shall flow out., While mixing, the water shall be gradually added and thoroughly mixed to form a stiff plastic mass of uniform colour so that each particle of sand shall be completely covered with a film of wet cement ratio shall be adopted as directed.

The mortar so prepared shall be used within 30 minutes of adding water. Only such quantity of mortar shall be prepared as can be used within 30 minutes.

## Stone course aggregate for nominal mix concrete

Coarse aggregate shall be machine-crushed stone of black trap of equivalent and be hard, strong, dense, durable, clean and free from skin and coating likely to prevent proper, adhesion of mortar.

The aggregate shall generally be cubical in shape. Unless special stones of particular quarries are mentioned aggregates shall be machine crushed from the best black trap of equivalent hard stone as approved. Aggregate shall have no deleterious reaction with cement. The size of the coarse aggregate for plain cement concrete and ordinary reinforced cement concrete shall generally be as per the  table  given  below. However in case of reinforced cement concrete the maximum limit may  be restricted to 6 mm less than the minimum lateral clear distance between bars of 6 mm less than the cover, whichever is smaller.

| I.S. Sieve nominal size Designation | Percentage by weight passing Sieve |  |  |
| --- | --- | --- | --- |
|  | 40mm | 20mm | 16mm |
| 80mm | - | - | - |
| 63mm | 100 | - | - |
| 40mm | 85-100 | 100 |  |
| 20mm | 0-20 |  | 85-100 |
| 12.5mm | - |  |  |
| 10mm | 0.5 | 0.02 | 0.3 |
| 4.75mm | - | 0.5 | 0.5 |
| 2.35mm | - | - | - |

## Note:-

This percentage may be varied somewhat but Engineer-in-charge when considered necessary for obtaining better density and strength of concrete.

The  grading  test  shall  be  taken  in  the  beginning  and  at  the  change  of  source  of materials. The necessary test indicated in I.S: 383-1970 and I.S: 456-2000 shall have to be carried out to ensure the acceptability. The aggregates shall be stored separately and handled in such a manner as to prevent the intermixing of different aggregates. If the aggregates are covered with dust, they shall be washed with water to make them clean.

The  necessary  tests  indicate  in  I.S.  383-1970  and  I.S.  456-2000  shall  have  to  be carried out to ensure the acceptability of the material.

If aggregate is covered with dust it shall be washed with water to make it clean.

## Black trap for equivalent hard stone course

Aggregate for Design Mix Concrete: Course aggregate shall be of machine crushed stone of black trap or equivalent hard stone and be hard strong dense, durable clean and free from skin and coating likely to prevent proper adhesion of mortar.

The aggregate shall generally be cubical in shape. Unless special stones of particular quarries are mentioned, aggregates shall be machine crushed from the

Best, black trap or equivalent hard stone as approved. Aggregate shall have no deleterious reaction with cement.

The  necessary  tests  indicated  in  I.S.  383-1970  and  I.S.  456-1978  shall  have  to  be carried out to ensure the acceptability of the material.

If aggregate is covered with dust it shall be washed with water to make it clean.

## Brick bats aggregate

Brickbat aggregate shall be broken from well burnt of slightly over burnt and dense brick. It shall be homogeneous in texture roughly cubical in shape, clean and free from dirt of any other foreign material. The brickbats shall be of 40 mm to 50 mm

size unless otherwise specified in the item. The under-burnt of over-burnt brick bats shall not be allowed.

The brickbats shall be measured by volume by suitable boxes of as directed.

  - BRICKS

Bricks shall be locally available first class bricks. Bricks shall be of size of 225 x 110 x 75 mm (9" x 4 3/8" x 2 3/4") unless otherwise specified. In all masonry works bricks of class designation 35 are to be used. Only bricks of one standard size shall be used on  one  work.  The  following  tolerances shall  be  permitted in  the  conventional size adopted in a particular work.

| Length | 1/8" (3.0 mm) |
| --- | --- |
| Width | 1/16" (1.50 mm) |
| Height | 1/16" (1.50 mm) |

The crushing strength of  the bricks shall  not  be  less than  35  kg/cm2. The  average water absorption shall not  be more than 20  percent by  weight. Necessary tests for crushing strength and water absorption etc. Shall be carried out as per I.S. 3495 (Part I to IV) 1976.

  - SHUTTERING

The shuttering shall be either of wooden planking of 30 mm minimum thickness with or without steel lining or of steel plates stiffened by steel angles. The shuttering shall be supported on battens and beams and props of vertical bellies properly cross-braced together so as to make the centring rigid. In place of belie props, brick pillar of adequate section built in mud mortar may be used.

The form work shall be sufficiently strong and shall have camber, so that it assumes correct shape after deposition of the concrete and shall be able to resist force caused by vibration of live load of men working over it and other incidental loads associated with it. The shuttering shall have smooth and eve surface and its joints shall not permit leakage of cement grout.

If at any stage of work during or after placing concrete in the structure, the form work

sags of bulges out beyond the required shape of the structure, the concrete shall be removed and work redone with fresh concrete and adequately rigid from work. The complete formwork shall be got inspected by and got approved from the Engineer- in-charge, before the reinforcement bars are placed in position.

The  props shall  consist of  bullies having 100  mm  minimum diameter measures at max length and 80 mm at thin end and shall be placed as per design requirement. These shall rest squarely on wooden sole plates 40 mm thick and minimum bearing area if 0-10 m2 lay on sufficiently hard base.

Double wedges shall further be provided between the sole plate and the wooden props so as to facilitate tightening and easing of shuttering without jerking the concrete.

The timber used in shuttering shall not be so dry as to absorb water from concrete and swell of bulge nor as green of wet as to shrink after creation. The timber shall be property sawn and planed on the sides and surface coming in contact with concrete / wooden form work with metal sheet timing of steel plates stiffened by steel angles shall be permitted.

As far as practicable, clamps shall be used to hold the forms together and use of nails and spikes avoided.

The surface of timber shuttering that would come in contact with concrete shall be well wetted and coated with soap solution before the concreting is done. Alternatively coat of raw linseed oil of approved manufacturer may be applied in place of soap solution. In case of steel shuttering either soap solutions of raw linseed oil shall be applied after thoroughly cleaning the surface. Under no circumstances black .of burnt oil shall be permitted.

The shuttering for beams and slabs shall have camber of 4 mm per meter (1 in 250) of as directed by the Engineer-n-charge so as to offset the subsequent deflection. For cantilevers, the camber at free end shall be 1750 of the projected length of as directed by the Engineer-in- change.

## Non Asbestos fibre flat shutters

Door  Shutters  of  Non  Asbestos  Fibre  Flat  Sheet  confirming  to  IS  14862-2000  of 16mm thick compressed and heat resistance both faces finished smooth incl. 16 gauge thick galvanized steel plain sheet lipping shall be provided all round the shutter (total

width of lipping (25+16+25) =66mm) incl. Iron oxidized fixtures and fastenings and Handles,  Aldrop,  Stopper  Tee  Hinges,  Door  Stop  etc.  All  as  approved  with  oil painting  in  three  coats  incl.  Priming  coat etc. Comp. As per detailed drawings and directed by Engineer-in-charge or Client. The thick of the shutters shall be uniform throughout with  a  permissible variation of  not  more than 0.8mm when measure at any two points.

  - GLASS

All glass shall be of the best quality, free from specks, bubbles, smokes, veins, air holes blisters and other defects. The king of glass to be used shall be mentioned in the item of specification of in to special provisions of as shown in detailed drawings. Thickness of glass panels shall be uniform the specifications of different kinds of glass shall be as under:

- In absence of any specified thickness of weight in the item of detailed specifications of the item of work, sheet glass shall be weighing 7.5 kg 1m2 for panes up to 600 mm x 600 mm.

- For panes larger than 600 mm x 600 mm and up to 800 mm x the glass weighing not less than 8.75 kg/m2 shall be used. For biggest panes up to 900 mm x 900 mm glass weighing not less than 11.25 kg/m2 shall be used.

- Sheet glass shall be patent flattened glass of best quality and for glazing and framing purpose shall conform to I.S. 1761-1960. Sheet glass of the specified colours shall be used, if so shown on detailed drawings of so specified. For important buildings and for panes with any dimension over 900 mm plate glass of specified thickness shall be used.

Glass shall be fluted or frosted glass as may be specified as required. The thickness and type of glass shall be as per details on drawings of as specified or as directed.

# EARTHWORK

## Extent and intent

The work under this section covers all operations listed below concerning the civil work and the site development work.

- Clearing and grubbing

- Grading

- Excavation including removal of top soil

- Filling and back filling

- Removal and disposal of surplus material

- Bringing sweet earth from outside where required

- Hard stone soling to floors and paving

The Construction Manager / Developer shall provide all materials, labour, equipment, Operations and incidental necessary and required for the completion of all aspects of Work listed above as called for in the drawings and specifications.

## General

The Developer shall visit the site, and decide for himself the nature of the ground and the subsoil to be excavated. No claim of extras will be entertained in consequence of any misunderstanding or incorrect information or ignorance of existing conditions.

## Antiquities

Any ancient carvings, relics, coins or other curiosities discovered during the excavation or other work shall remain the property of the Owner and shall be handed over to the Owner of Work.

## Excavated materials

Any sand, gravel of similar useful materials obtained from excavation site shall be the property of the Owner and shall not disposed of or used in the construction of the works without prior written consent of the Owner of Work. It is the intention of this contract that all benefits accruing from materials within the site shall pass to the Owner and the fair market price of any such material disposed of or used shall be alleged to the Owner by the Developer and the contract sum adjusted accordingly. Borrow pits shall not be dug on the site without the prior written consent of the Owner of Work.

## Clearing

The Developer shall clear the site of all rubbish and unwanted civil work. All disused foundation drains of other obstructions met with during excavation shall be dug out and cleared at Developer's own expense.

## Benchmarks

The construction Manager / Developer shall erect sufficient permanent benchmarks in suitable locations for all the works before starting work, from which all the important levels shall be laid out. A qualified surveyor shall be engaged by the Developer to locate all buildings, paths, roads, utility lines, etc. Developer shall provide all pegs, flags, pillars and labour required for setting out.

# FILLING

## Earth filling (by excavated earth)

The work shall be taken up after the building has reached up to plinth stage or the floor level,  as  the  case  may  be.  The  space  between  the  walls  shall  be  filled  in  with  the approved earth (excavated earth) in layers of 150mm to 200mm (6” to 8”) thick to required level, each layer watered and consolidated properly before putting next layer. No lumps, clods or rubbish are to be used in filling. After filling, the area to be flooded with water for a day to enable the filling to be thoroughly consolidated and allowed to get sufficiently dry after which ramming and levelling as directed by Engineer shall be done. Filling in basement over raft foundation will also come under this item.

## Earth filling (Earth material brought from outside)

If the earth has to be bought from outside of the site, the rate includes the purchase cost of the earth, loading and unloading, its carting from outside to site, octroi, levy royalty  or  any  other  form  of  taxes  as  per  prevailing  rules,  screening  if  necessary, spreading  in  150mm  to  200mm  (6”  to  8”)  layers  and  watering,  ramming  and consolidating with 10 ton roller, if it not possible then through electric compactors of adequate  capacity.  Each  layer  prior  to  putting  next  layers  as  per  the  instruction  of Engineer. The earth shall be got provided prior to bring on site. The earth shall be free from trees roots, weeds, big stones, and other objectionable materials liable to decay.

## Cinder filling

The work shall be carried out after the building is constructed up to plinth or the floor levels or at terrace or toilet sunk slab level as the case may be and the space required is  filled  up  with  cinder  brought  from  outside  to  the  required  level  and  then  it  is properly watered and consolidated in the layers of 150 mm (6”) wood ash, dirt and

foreign matters. Cinder should be ground fine and screened through sieve of 9 meshes per Sq. Cm. (64 meshes per sq. In) and residue in the sieve should be rejected. Cinder shall not contain more than 10% if un-burnt carbon (combustible matter).

# CONCRETE WORK

## Extent and intent

The Developer shall provide all labour, materials, operations, equipment and incidentals necessary and required for the completion of all concrete work called for.

## General

It  is  the  intent  of  this  specification  to  ensure  that  all  concrete  placed  at  various locations  on  the  job  should  be  durable  and  strong.  It  should  wear  well  and  be practically  impervious  to  water.  It  should  be  free  from  such  defects  as  shrinkage, cracking, honeycombing, all plain and reinforced concrete shall conform in all respects to Indian standard 456-2000.

## Materials

Cement: Ordinary / rapid hardening Ordinary Portland Cement of 43 Grade as per conforming to IS: 8112-1976 or Ordinary Portland Cement of 53 Grade conforming to IS: 12269-1976 shall be used. Cement shall have uniform colour. Cement shall be fresh when delivered at site. Consignment shall be used in order or delivery. Admixtures (such  as  accelerators,  retarders,  waterproofing  compounds,  etc.,)  shall  be  as  far  as possible  avoided,  where  its  use  is  considered  unavoidable  it  may  be  used  only  if approved by the Architect and Structural Designer and subject to IS: 456-2000.

Water: Water used for mixing concrete shall be in accordance with clause 4/3 of IS: 456-2000. The Construction Manager / Developer shall produce Test Results for the mixing  of  water  used  on  the  job,  when  requested  by  the  OWNER  OF  WORK  or Structural Designer.

Aggregates: Aggregates (fine and course) should be had and should not contain materials that are likely to decompose or change in volume when exposed to water or to affect the reinforcement. All aggregates shall be clean and free from organic impurities. The aggregates shall be free from coatings or dust and clay. Coarse aggregate shall be machine crushed hard stone and fine aggregate shall be coarse rover

are pit sand, and both obtained from approved source. Aggregates shall be screened and washed by mechanically operated equipment, if the deleterious materials content exceeds 5 percent by volume. All aggregates used shall conform to IS: 383-1979. If the aggregates are wet, due allowance shall be made for bulking in accordance with IS: 2386-1963  (Part  III)  unless  otherwise  specified,  the  size  of  coarse  aggregates  shall conform to clause 4.2 of IS: 456-2000. All aggregates shall be suitably rated from the maximum  certified  gauge  to  the  minimum.  The  construction  Manager  /  Developer shall submit a sieve analysis of the aggregates to be used on the works and maintain a regular record of sieve analysis during the currency to the work. The grading of the aggregates will be determined from these sieve analyses to produce maximum density of concrete. All expenses of sieve analysis, mix design and trial mixes shall be borne by the developer.

## Storage

Cement shall be stored in accordance with clause 5.1 of IS: 269V1967. Any cement, which has become wet, show any sign of caking, or deterioration, of contamination of any kind shall not be used, and shall be immediately removed from the site. Fine and coarse aggregates shall be stored in separate open bins scoring to sizes. The bins shall have brick wall of adequate thickness and floor paved with flat bricks.

## Batching

In the case of ordinary concrete, aggregates shall be measured by volume, cement by weight  (density  of  cement  assumed  to  be  1.44  kg/liter.  (A.  50-kg  bag  of  cement contains 35 liters). Mixing water shall be measured in graduated liter cans.

## Mix proportions

All  concrete  not  specifically  designated  as  controlled  concrete  shall  be  treated  as ordinary  concrete  of  nominal  mix  as  specified.  Where  nominal  concrete  mixes  are described as 1:1.5:3, 1:2:4, 1:3:6, 1:4:8, etc., the figures denote the relative properties of cement, dry sand and graded stone aggregate respectively. For example, concrete of nominal mix 1:2:4 shall mean a mix of 1 part cement, 2 part of washed dry coarse and and 4 parts crushed graded stone aggregate, the proportion being volumetric.

The cement shall be measured by weight, and aggregates shall be measured in properly constructed gauge boxes. If sand is wet, necessary allowance shall be made for bulking.

The  size  of  aggregates  shall  be  20  mm  and  downgraded  suitably  to  achieve  dense concrete.

All aggregates and cement shall be measured by weights in approved high-batching equipment and water shall be measured in graduated, liter cans.

| Grade of concrete | Minimum Compressive Strength of 15 cm cubes at 28 days |  |
| --- | --- | --- |
|  | Preliminary (Trial) Cubes | Test work (Test) Cubes |
| M150 | 200 Kg/cm2 | 150 Kg/cm2 |
| M200 | 260 Kg/cm2 | 200 Kg/cm2 |
| M250 | 320 Kg/cm2 | 250 Kg/cm2 |
| M300 | 380 Kg/cm2 | 300 Kg/cm2 |
| M350 | 440 Kg/cm2 | 350 Kg/cm2 |

## Water-cement ratio

The water-cement ration shall be carefully controlled throughout the work. This calls for a regular check on the equipment used for measuring water. Only guaranteed liter cans shall be used for this purpose.

In the case of 'ordinary' concrete, the maximum value of water-cement ration shall be

0.50 and in the case of 'controlled' the water-cement ration as determined by the mix design shall be strictly adhered to. While determining the amount of mixing water, moisture content of aggregates shall be taken into account. Additional water if water, moisture content of aggregates shall be taken into account. Additional water if used to improve to workability shall be accompanied by an equal volume of cement. In any case, such additional use of water shall be subject to approval of the Architect and Structural Designer.

## Mixing

All concrete, whether plain or reinforced, ordinary of controlled, shall be mixed in a standard type box mixer, having minimum drum speed of 60 peripheral meters per minute. The cement and aggregates shall be first mixed dry until all articles of

aggregate are coated with cement. Mixing water shall be added and mixing continued for at least two to twelve minutes to from concrete of a uniform colour and consistency.

## Transportation

Concrete  shall  be  placed  in  its  final  position  within  20  minutes  of  mixing.  The Construction Manager shall arrange his mixer position and a method of transportation to  ensure  that  this  period  is  not  exceeded  under  any  circumstance.  Transportation should be smooth and free from jolting, so that there is no segregation or loss of any of the ingredients.

## Placing concrete

The  forms  shall  be  well  wetted  before  placing  concrete.  Concrete  should  not  be dropped from a height greater than 1 meter. Properly constructed chute shall be used in such cases where it is necessary to exceed this height. Concrete must be thoroughly worked into the forms so that they are entirely filled; reinforcing bars adequately and tightly surrounded and entrained air released from the mass of concrete. Placing shall be carried out by hand punning as well as vibrators in the manner directed by Architect or Structural Designer. Concrete should not be moved any considerable distance in the moulds, being consolidated as nearly as possible in the place where it is dumped. The full depth of any lift shall be replaced at one pouring. In casting beams or other deep sections, concrete shall not be placed in layers.

## Consolidation

All  plain  and  reinforced  concrete  shall  be  consolidated  by  means  of  mechanical vibration. Adequate number of vibrators shall be used to ensure full compaction of concrete in about 10 minutes of placing. If immersion vibrators are used, these shall be inserted at places not exceeding half meter apart until it is immersed to the full depth   of   concrete.   Wherever   possible   shutter   vibrators   shall   be   used   and   the construction  Manager  shall  design  his  shuttering  so  that  this  can  withstand  form vibration.  Care  shall  be  taken  to  ensure  that  concrete  is  not  over-vibrated  to  avoid segregation. In addition to mechanical vibration, sufficient hand tools must be used to ensure full consolidation around reinforcement and at all edges and corners.

## Testing

Comprehensive strength, water absorption test an dimension test has to be carried out as per the relevant I.S. specifications for purchase of every one lakh bricks or part thereof, at the cost of Developer from the Government approved laboratory as directed by the Architect / Structural Designer.

# PLASTER WORK

## Extent and intent

The Developer shall furnish all materials, labour, scaffolding, equipment, tools, plant and incidentals necessary and required for the completion of all plaster and wall finishes. The Developer shall be responsible to take proper precautions to protect already installed work from damage.

## General

Plaster as here in specified shall be applied to all internal and external surfaces where called for Glazed tile dado, terrazzo dado, and other wall finishes are to be provided where indicated on drawings and schedules. Areas called for on drawings and typical shall be considered to apply to appropriate, adjoining areas whether shown on same drawings or not and whether indicated or not. All plaster work and other wall finishes shall be executed by skilled workmen in a workman like manner and shall be of the best workmanship and in strict accordance with the dimensions on drawing.

## Plaster work

The primary requirements of the plaster work shall be to provide an absolutely water tight enclosure, dense, smooth and hard and devoid of cracks on the interior and exterior. The Developer shall do all that is necessary to ensure this result. All plastering shall be finished to true plane, without imperfections and square with adjoining work and shall form proper foundations for finishing materials such as paint etc.

Masonry and concrete surfaces to which plaster is to be applied shall be clean, free from efflorescence, damp and sufficiently rough and keyed to ensure proper bond.

Wherever directed all joints between concrete frames and masonry in filling shall be expressed by a groove cut in the plaster. Said groove to exactly coincide with the joint beneath.

Where grooves are not called for the joints between concrete members and masonry in filling shall be covered by 245 gauges galvanized chicken-mesh strips 40mm wide or as shown, installed before plastering.

## Chasing

All chasing, installation of conduits, boxes etc. To be completed before any plastering or other wall finish is commenced on a surface. Chasing or cutting of plaster or other finish will not be permitted. Broken corners shall be cut back not less than 150mm on both  sides  and  patched  with  Plaster  of  Paris  or  rich  cement  paste  as  directed.  All corners shall be rounded to a radius of 8 mm or as directed by the Architect.

## Samples

Samples of each type of plaster and other wall finishes shall be prepared for approval of the Architect.

## Materials

Cement: As specified under concrete work Water:	As specified under concrete work.

Sand:	Washed fine sand and / or stone aggregate as called for sand and stone aggregate to conform to the requirements given under "concrete work"

## Proportions

The materials used for plastering shall be proportioned by volume by means of gauge boxes.

## Preparation of Surface

The joints in all walls, both existing and freshly built shall be raked into a depth of 15mm brushed clean with wire brushes dusted and thoroughly washed before starting plaster work. Concrete surfaces shall be roughened by hacking over the entire surface shall be roughened by hacking over the entire surface as approved by the Architect to ensure proper key for the plaster.

## Mortar Mixing

Mortar shall be prepared as specified under "Brick Work" it shall be made in small quantities only as required and applied within 15 minutes of mixing

## Appliances

Plaster application shall be commenced only after the preparatory work is approved by the Architect. Correct thickness of plaster shall be obtained by laying plaster screeds gauges at intervals of 1.50 meters. Mortar shall be firmly applied, well pressed into the joints, rubbed and finished as approved by the Architect to give a smooth and even surface.

## Curing

Finished plaster shall be kept wet for 10 day after completion. In hot weather walls exposed to sun shall be screened with matting kept wet or any other approved means.

## Water Proof Cement Plaster:

Specifications are same as stated above but the waterproof compound like OCNFLOW SNW2,  JK  WATER  PROOF  or  any  other  approved  quality  shall  be  mixed  with  dry cement at the rate specified by the manufacturer.

## Normal Cement Plaster (in one coat)

This plaster is to be laid in one coat of 12mm thick in Cement Mortar 1:4, 1 Cement: 4 fine sand, on the surface prepared for plaster and following all the norms as stated above in 1. PLASTER

## Cement Plaster with Neeru + Cement finish

This kind of Plaster is normally for interior side or as specified location by Client to be applied  as above 2. NORMAL CEMENT PLASTER and the surface shall  be rubbed smooth after coating it with a thick coat of pure Portland cement slurry while the base coat is still fresh. If Neeru plus cement finish is specified floating with neat cement will not be required.

## Sand face plaster (Cement Plaster in Double coat)

This plaster is to be laid in double coat in 20mm thick in cement mortar.    Rough and fine sand plaster in single coat on shall be 12mm thick backing coat made by mixing one part of cement to three parts of clean fine sand for coat the ingredients shall be

workable mix is obtained. And 8mm thick finishing coat at of cement mortar made by mixing one part of cement & two parts of clean fine sand. The plastered surfaces will be completed by means of sponges to obtain an even and granular surface all over. The entire plasterwork shall be done to perfect plumb. The sides of windows, openings such as jambs, and reveal sun breakers, drop paradis, fins, chhajjas and the like, around externally shall be finished as directed by the Client / Engineer- in-charge and shall be included in the rate of this item.

The plaster shall be thoroughly cured for 14 days as directed by Client / Engineer-in- charge. Any cracks which appear in the surface and all portions which sound hollow, when  tapped  or  are  found  to  be  soft  or  otherwise  defective,  shall  be  cut  out  in rectangular shape and redone as directed by the Client / Engineer-in-charge.

# FINISHES

## Extent and intent

The Developer shall supply all materials, labour, tools, ladders, scaffolding and other equipment necessary for the completion and protection of all painting / finishing work. Painting & finishing, as herein specified shall be applied to all surfaces requiring painting / finishing throughout the interior and exterior of the buildings as given in the schedule of finishes or elsewhere. The painting / finishing shall be carried out by a specialist sub-developer, approved by the Architect.

## Storage

Storage of materials to be used on the job shall be, only in a single place approved by the Architect. Such storage place shall not be located within any of the buildings included in the contract.

## Materials

Materials used in the work shall be of manufacture approved by the Architect, Ready mixed paints, varnishes, enamels, lacquers, stains, paste fillers, distempers and other materials must be delivered to the job site in the original containers, with the seals unbroken and labels intact. Each container shall give the manufacturer's name, type of paint, colour of paint and instructions of reducing. Thinning shall be done only in

accordance with directions & manufacturer's specification. Remove rejected materials immediately from the premises.

## Shades

All shades, as provided in the shade schedule, shall be approved by the Architect. The Developer shall as far as possible use pre-mixed manufacturer's shades and shall prepare sample of the shades selected and submit same for approval by the Architect. No work is to proceed until the Architect has given his approval, preferably in writing, of the shade samples.

## Commencement of work

Painting / finishing shall not be started until the surfaces to be painted / finished are in a condition fit to receive painting / finishing and so certified by the Architect.

Painting / finishing work shall be taken in hand only after all other civil work is completed.

Buildings where painting / finishing work is to commenced shall be thoroughly swept and cleaned up before commencement of painting / finishing.

## Scaffolding

Only double scaffolding having two sets of vertical supports shall be provided for all, painting / finishing work. The supports shall be tied together with horizontal pieces over which the scaffolding planks shall be fixed.

All the vertical and horizontal members of the scaffolding shall be placed sufficiently away from the surfaces to be painted to ensure proper and unit erupted application.

## Workmanship

The workmanship shall be of the very best; all materials evenly spread and smoothly flowed as without running sags, using good quality tools, brushes, etc., as required. Only skilled painters / applicators shall be employed. A properly qualified foreman shall be constantly on the job whilst the work is proceeding. All surfaces to be painted

/ finished shall be cleaned free of all loose dirt and dust before painting / finishing is started. AII work where a coat of material has been applied must be inspected and approved before application of the succeeding specified coat. Each undercoat shall be distinct shade of the approved colour.

Before painting / finishing, remove hardware, accessories, plates and similar items or provide portion to all such items. Upon completion of each space, replace all fixtures removed. Remove doors if necessary to paint bottom edge. Use only skilled mechanics for the removal and replacement of above items.

## Concealed surfaces

All interior and exterior trim, door frames, doors, shelving, cabinet work shall be thoroughly and carefully back painted as all surfaces and edges which will be concealed when installed. Such surfaces shall be clean, dry, sanded and properly prepared to receive the paint. Tops, bottom and edges of doors shall be finished same as the rest of the door.

## Protect and clean

The agency shall protect not only his own work at all times, but shall also protect all adjacent work and materials by suitable covering during progress of his work. Upon completion of his work, he shall remove all paint and varnish spots from floors, glass and other surfaces. Any defaced surfaces shall be cleaned and the original finish restored. He shall remove from the premises all rubbish and accumulated material and shall leave the work in clean, orderly and acceptable conditions.

# PREPARATION OF SURFACES

PLASTER WORK: Fill all holes, cracks and abrasions with plaster of parish / cement slurry as directed, properly prepared and applied and smoothed off to match adjoining

surfaces. Do not use sand paper on plaster surfaces. Plaster shall be allowed to dry for at least 12 (twelve) weeks before the application of paint / finishes.

STEEL AND IRON: All surfaces shall be washed with mineral spirits to remove any dirt or grease before applying paint. Where rust or scale is present, it shall be wire brushed and sand papered clean. All cleaned surfaces shall be given one coat of approved phosphate before prime coat in accordance with the manufacturers, Instructions. Shop coats of paint that have become marred shall be cleaned off, wire brushed, and spot primed over the affected areas.

## Application

The paint shall be continuously stirred in the container so that its consistency is kept uniform throughout. The painting / finishing shall be laid on evenly and smoothly by means of crossing and laying off, the latter in the direction of the grain of the wood. The crossing and laying off consists of covering the area with paint, brushing the surface hard for the first time and then brushing alternatively in opposite directions, two or three times and then finally brushing lightly in a direction at right angles to the same. In this process no brush marks shall be left after the laying off is finished. The full process of crossing and laying off will constitute one coat.

Where so stipulated, the painting / finishing shall be carried out using spray machines suited for the nature and location of the work to be carried out. Only skilled and experienced workmen shall be employed for this class of work. Paints used shall be brought to the requisite consistency by adding a suitable thinner. Spraying shall be carried out only in dry conditions. No exterior painting / finishing shall be done in damp foggy or rainy weather. Surface to be painted shall be clean, dry, smooth and adequately protected from dampness. Each coat shall be applied in sufficient quantity to obtain complete coverage, shall be well brushed and evenly worked out over the entire surface and into all corners, angles and crevices allowed to thoroughly dry. Second coat shall be of suitable shade to match final colour, and shall be approved by the Architect before final coat is started. Allow at least 48 hours drying time between coats for interior and 7 days for exterior work, and if in the judgment of the Architect more time is requested it shall be allowed. Finished surfaces shall be protected from dampness and dust until completely dry. Finished work shall be uniform of approved

colour, smooth and free from runs, sags, defective brushing and clogging. Make edges of paints adjoining materials of colours sharp and clean, without overlapping.

In order to achieve a superior finished surface, putty paste fillers shall be used on, all surfaces to be painted. To fill pores, dents, etc. The putty / paste fillers shall be approved quality and manufacture and shall be applied to the surface with a knife or other sharp edged tools after the priming coat as well as after each undercoat. The surface, after filling with putty / paste tiller, shall be rubbed down with fine sand paper and dusted off before the application of the subsequent coat.

Paste wood filler when set shall be wiped across the grains of the wood and then with the grain to secure a clean surface. Surface to be stained shall be covered with uniform coat of stain wiped off if required.

FINISH: The painted surfaces shall be finished to require texture. Matt finish shall be achieved by use of sponge rollers or stippling brushes as called for.

## Types of Paint Finishes Enamel paints:

Non-Galvanized Steel Surfaces: Coat of red oxide primer after phosphate followed by the three or more coats of synthetic enamel paint. Paste filler to be applied after every coat excepting final finishing coat and sanded

## White washing

White Washing with lime on decorated wall surfaces (two coats) to have given an even shade including thoroughly booming the surface to remove all dirt, dust, mortar drops and other foreign matter.

## Materials:

The clear collie shall be made from glue and boiling water by Mixing 1 Kg. Mixture shall be suitably tinted where required for use under colour distemper if directed. Glue shall conform to I.S. 852-1969 (Specifications for animal glue). 1.2 Lime used shall be freshly burnt glass ‘C’ Lime (fat lime) and white in colour conforming to I.S. 7121973. Best quality of gum shall be used in the preparation of white wash. Ultramarine blue or  Indigo:  This  shall  conform  to  I.S.  55-1970  for  points,  and  shall  be  used  for

preparation of white wash, Pigments: Mineral colours, not affected by lime shall be used in preparing colour wash.

## Workmanship:

Preparation of white wash solution:

Surface already white or colour. The fat lime shall be slaked at site and shall be mixed and stirred with about five liters of water for 1 Kg. Have unslaked lime to make a thin cream.  This  shall  be  allowed  to  stand  for  a  period  of  24  hours  and  then  shall  be screened through a clean coarse cloth, 4 Kg. Of gum dissolved in hot water shall be added to each cubic meter of lime cream. Small quantity of ultramarine burnt *Up to 3 gms. Per Kg. Of lime) shall also be added to the last two coats of white wash solution and the whole solution shall be stirred thoroughly before use.

## Preparation of surface:

The surface shall be thoroughly cleaned of all dust, dirt, mortar cropping and other foreign matter before white wash is to be applied.

The surface spoiled by smoke soot shall be scrapped with steel wire brushes or steel scrapers or shall be rubbed with over burnt surkhi or brickbats. The surface shall be then boomed to remove all dust, dirt and shall be washed with clean water.

Oil or grease spots shall be removed by suitable chemical and smooth surface shall be rubbed with wire brushes.

All unsound portion of the surface plaster shall be removed to full depth of plaster in rectangular patches and plastered again after raking the masonry joints properly. Such portion shall be wetted and allowed to dry. They shall then be given one coat of white wash.

All unnecessary nails shall be removed; the holes cracks patches etc. Shall be made good with materials similar in composition to the surface to be prepared.

## Scaffolding:

Wherever scaffolding is necessary it shall be erected in such a way that as far as possible on part of scaffolding shall rest against the surface to be white or colour washed. A properly secured strong and well-tied suspended platform (Zoola) may be used for white washing. Where ladders are used, pieces of old gunny bags shall be tied

at top and bottom to prevent scratches to the floors and walls. For white washing of ceilings proper stage scaffolding shall be reacted where necessary.

## Application of white Wash:

On the surface so prepared the white wash shall be applied with “Moon” brush. The first stoke of the brush shall be from top down wards, another from bottom upwards over the first stroke and similarly one stroke from the right another from the left, over the first stroke brush before it dries. This will from one coat. Each coat shall be allowed to dry before next coat is applied. Number of coats as specified in item shall be applied. It shall present smooth and uniform finish free from brush marks and it should not come off easily when rubbed with finger. Splashing and dropping if any on the doors and windows, ventilators etc. Shall be removed and the surface cleaned. Priming and Alkali resistant treatments, scraping of surface washing etc. Surface spoiled by smoke soot removed of oil and grist spouts treatment for infection with efflorescence moulds moss, fungi algae and lichens and patch repairs to plaster wherever done shall not be paid extra.

## Water Proof Cement Paint

Water proof cement paint shall be of approved brand (like Snowcem etc.) And manufacture and of required shade, enlisted by the Client / Engineer-in-charge.

## Preparation of Surface:

For new work, the surface shall be thoroughly cleaned of all mortar dropping, dirt, grease and other foreign matter by rushing and washing. The surface shall be wetted by a sprinkling of water or water with fine spray. The surface shall be sprayed several times with a few minutes’ intervals between each spraying to allow moisture to soak into the surface.

## Preparation of mix:

Waterproof cement paint shall be mixed in such quantities as can be used up within an hour of its mixing as otherwise the mixture will set and thicken, affecting flow and finish. Waterproof cement paint shall be mixed with water in two stages. The first stage shall comprise of two parts of water stirred thoroughly and allowed to stand for five minutes, care shall be taken to add the water proof cement paint gradually to the water and not vice-e-versa. The second stage shall comprise of adding further one part of

water to the mix and stirring thoroughly to obtain a liquid of workable and in uniform consistency. In all cases the manufacturer’s instructions shall be followed meticulously.

The lids of cement paint drums shall be kept tightly closed when not in use, as by exposure to atmosphere the cement paint rapidly becomes air set due to its hydroscopic qualities.

## Application:

The  solution  shall  be  applied  on  the  clean  and  wetted  surface  with  hairbrushes  or spraying  machine.  The  solution  shall  be  kept  well  stirred  during  the  period  of application. It shall be applied on the surface, which is under shadow of the building so that the direct heat of the sun on the surface is avoided. The method of application of waterproof cement paint shall be similarity to oil bound distemper. The completed surface  shall  be  watered  after  the  day’s  work.  After  the  first  coat  of  paints  has hardened, it shall be wetted again before the application of second coat, at least 24 hours should elapse between the two coats. The watering should be done at least for seven days  till  the paint  gets required  strength. For new work, the surface  shall  be treated with three or more coats of waterproof cement paint as found necessary to get a uniform shade.

# STEEL WORK

## Extent and intent

The Developer shall furnish all materials, labour, operations, equipment, tools, plant and incidentals necessary and required for the completion of all metal work in connection with railing and window and other items of metal work as called for in the drawings. The supplying of additional fastenings, accessory, features and other items not mentioned specifically herein but which are necessary to make a complete installation shall be part of this contract.

## General

All metal work shall be free from defects impairing strength, durability and appearance and shall be of the best commercial quality for purposes specified. Made with structural properties to withstand safely strains, tresses to which they shall be normally subjected.

## Samples

Samples of all typical metal work, such as windows glazing, flashing railing etc., shall be fabricated, assembled and erected or submitted to the Architect as directed by him, for his approval.

## Approved manufacturers

All floors, windows, railings and other work shall be manufactured by an approved manufacturer / fabricator. The entire work shall be carried out by workmen skilled in this kind of work in a shop fully equipped to carry out all phases of fabrication in accordance with the best accept practices.

## Fittings

Hinges, locks, handles, stays and other fittings shall be provided as called for in the schedule of hardware / drawings.

## Fixing

The Developer shall fix windows, etc., in prepared openings. Steel window frames, wherever possible, shall be fixed in place before erecting partitions. Where this is not possible, prepared openings shall be left for hold-fasts. Breaking of partitions or walls

for fixed to column / wall faces they shall be fixed with raw bolts / expansions bolts of approved make in approved manner. The Developer shall be responsible for assembling composites, bedding and pointing with mastic inside and outside at the mullions and transoms, fixing lugs to the frames, placing the windows in their respective openings and bedding with mastic. The Developer shall be responsible for all builders work including all cutting out and making good, forming fixing holes for inserting loose lugs, bolts and clips and for stacking of windows, adjacent to the opening for necessary hoisting. The Developer shall be responsible for the windows being set straight, plumb and level and for their satisfactory operation after operation after the fixing is complete.

## Railing

Mild steel and other types of railing called for on the drawings shall be executed by craftsmen specially trained in the trade in a shop fully equipped to carry out all phases of fabrication in accordance with the best accept practices and as shown on the drawings. All work, as far as possible shall be shop fabricated and brought on site for erection. The railings shall be assembled square true to proper plan or curved to the radius shown on the drawings. Joining methods shall be flush type designed to produce an adequately strong for a particular application, and approved by the Architect.

Welding shall be executed from the non-exposed side, as far as possible and in each case the welds shall be ground smooth and finished with a texture matching the parent metal. All welds shall be finished smooth and square.

## Painting

All windows, louvers, railing etc. Shall be phosphate and given two coats of red oxide primer in the shop before dispatch and shall be enamel painted as per specifications after installation

## All steel must be TMT bars

TMT bars reinforcement for RCC work shall conform to I.S. 432 (part-II) 1966 and shall be of tested quality. It shall also comply with relevant part of I.S. 456-2000.

All the reinforcement shall be clean and free from-dirt, paint, and grease, mill scale of loose or thick rust at the time of placing.

## High tensile steel wire

The high tensile wires for the use in pre-stressed concrete work shall conform to I.S. 2090-1962. The tensile strength, of the high tensile steel bars shall be as specified in the item. In absence of the given strength, the minimum strength shall be taken as per Para 6.1 of I.S. 1985-1962. Testing shall be done as per I.S. requirements.

The high tensile steel shall be free from loose mill scale, rust oil, grease, or any other harmful matter. Cleaning of steel bars may be carried out by immersion in solvent solution, wire brushing of passing through a pressure box containing carborundum.

The high tensile wire shall be obtained from manufactures in coil having diameter not less than 350 times the diameter of wire itself so that wire springs back straight on being uncoiled.

## Mild steel binding wire

The mild steel wire shall be of 1.63 mm of 1.22 mm (16 of 18 gauges) diameter and shall conform to I.S. 280-1972.

The use of black wire will be permitted for binding reinforcement bars. It shall be free from rust, oil paint, grease, loose mill scale or any other undesirable coating that may prevent adhesion of cement mortar.

## Structural steel

All structural steel shall conform to I.S. 2062-1965. The steel shall be free from the defects mentioned in I.S. 226-1975 and shall have a smooth finish. The material shall be Rivet bars shall conform to I.S. 1148-1973.

When the Contractor supplies the steel, test certificates of the manufactures shall be obtained according to I.S. 226-1975 and other relevant Indian Standards.

# ELECTRIFICATION

## General

The work shall be carried out as per C.P.W.D. specifications of electrical works 1972 for internal E.I. the Indian electricity rule 1956 as amended up to date for such work, unless otherwise specified in writing by the O.O.W.

All materials should be of ISI mark/standard and of approved quality.

The run of the cables position of junction boxes, fittings etc. should be approved by the

O.O.W. The layout of the above should be marked on the site and approved by the

O.O.W. before actual execution.

Persons executing electrical work should have electrical license as required according to IE Ac.

The earthing should be done in presence of the O.O.W. or his authorized Representative.

Contractor shall quote rates of item no.37 including cost of all materials and labour charges of following item in point included

- Point wiring with 1.0mm2 copper PVC insulated-wires with 1.0mm2 copper

PVC insulated wire for earth continuity in PVC casing capping having double locking arrangement with grooves, trucking of as per ISI for light & fan.

Complete with 5A tissino type shockproof accessories erected on polished wooden block covered with 3mm thick laminated sheet.

- Point wiring with 1.0mm2 copper PVC insulated-wires with 1.0mm2 copper

PVC insulated wire for earth continuity in PVC casing capping having double locking arrangement with grooves, trucking of as per ISI for plug with tissiono type shock proof 3 pin socket & switch 5 Amp. Erected & polish wooden block covered with 3mm thick laminated sheet.

- Mains with ISI marked copper conductor PVC insulated wire in PVC casing capping erected with copper conductor PVC insulated wire for earth continuing of following size 2wire 1.5mm

2, 2 wire 2.5mm.

- All internal wiring are open in PVC casing capping.

- 240V MCB Double pole switch. 6 to 32 Amp. With enclosure – 17 nos. each block.

- Steel meter box with shutter and locking arrangement size of meter box of 17 nos. of meter box fixing required size – 1 no. each block.

Completion certificate and test report must be submitted after the end of the works or during the execution as per requirement of the O.O.W.

## Medium voltage distribution system (internal lighting & power wiring) General

Medium voltage distribution system shall be applicable for wiring 3 phase, 4 wire440 Volts, 50 HZ. A.C. supply & single phase, 2 wire 240 Volts, 50 HZ. A. C. supply.

## Regulations & Standards

The  system  shall  be  governed  by  the  requirements  of  1S:732:  I.E.  rules,  &  lEE regulations. I.S. standard & codes applicable for medium voltage distribution is also listed in standard specification.

## PVC casing capping & accessories

The thickness of PVC conduits shall be as follows 40 mm dia. 1.5 mm

32 mm dia. 1.5 mm

25 mm dia. 1.5 mm

20 mm dia. 1.5 mm

15 mm dia. 1.5 mm

## Wiring Conductors

All wiring conductors shall be PVC insulated, standard copper conductors of 650 V/1100V grade. Wiring conductors shall be confirmed in all respects to IS: 694.

The current rating for wiring conductors shall be based on the following Parameters

- Ambient temperature 40° C.

- Conductor temperature 70° C.

Wiring  conductors  shall  be  supplied  in  red,  black,  yellow,  blue  colours  for  easy Identification of wires. The wiring conductors shall be supplied in sealed coils of 100

m. length. The wiring conductor shall bear manufacturer's trade mark name, ISI mark, voltage grade etc.

Wiring for power, lighting circuits, television systems shall be carried out in Separate and distinct wiring system.

The wiring system envisaged will be generally shown on the layout drawings and line diagrams, however, a brief account of the general wiring system is

Given below:-

- SUBMAINS WIRING

Wiring from switch board to the individual distribution board.

- CIRCUIT WIRING

Wiring from DBs to the points control boxes for lighting, fans, SA socket etc. And from DBs to the power sockets in the case of power wiring.

The sub-main wiring shall  be single phase 2  wire system. Each sub-main wiring  m circuit  shall  als0  have  its  own  copper  earth  continuity  wire.  The  number  &  size  of copper earth continuity wire shall be as per the detailed drawings and

Standard specification.

Circuit wiring shall generally be of single phase system. However a maximum of 3 to 4 single phase circuits belonging to the same phase/pole could be installed in the same conduit or race-way. Each circuit wiring shall be provided with suitable copper earth continuity conductor as per standard specification

No. ADF-150-85. Not more than eight light points/fan points shall be grouped on one lighting circuits. The load per circuit shall not exceed 800 watts. The minimum size of conductor for wiring of lighting circuits shall not be less than 1.5 mm in case of copper

conductor. Power wiring shall not have than one sockets connected to one circuit. AII the wiring shall be carried out in looping in-loop system. .

The maximum number of various size conductors that could be drawn in to various sizes of conduits shall be as per table II of IS: 732. The wiring shall be colour coded for easy identification of phases and neutral. The following colour code shall be adopted.

Phase	R Red

Y Yellow / White B Blue

Neutral	Black

Earth	Green

The circuit wiring may be separately measured or included in point wiring as per the nomenclature specified in BOQ.

## Switches, Sockets & Accessories General Requirements

Light control switches shall be 5A rating for controlling up to four light points and 15A rating for more than four light points. Light control switches shall be of piano key type design suitable for flush mounting for general lighting. Wherever specifically called for tumbles type switches shall be used for surface mounting.

Light control shall have either integral mounting plates or white PVC/Perspex plates as specified / approved.

All  sockets  6A  & 16A ratings  shall  be  flush mounting  type  with  control  switches  of piano key type design of the same rating as that of the sockets. All sockets outlets shall be of 5 pin type. The base of the socket shall be of high quality porcelain with pins made of brass. Sockets shall be provided with PVC surface plates with round comers and bevelled edges. All the sockets shall be provided with plug tops of approved quality and design.

## Lamp Holders, Ceiling Roses etc.

Accessories for, light outlets such as lamp holders, ceiling roses etc. shall be inconformity with requirements of specifications. Only approved make of accessories shall be supplied.

## Installation of Switches, Socket & Accessories

All the switches shall be wired on phase. Connections shall be made only after testing the wires for continuity, cross phase etc. with the help of meter. Switches, sockets, fan regulator etc. shall be housed in proper approved. Teakwood / PVC / metal box with PVC / Perspex sheet plates. Regulators shall be fixed on adjustable MS flat straps inside the enclosure. The arrangement of switches and sockets shall be neat and systematic. Covers for enclosures accommodating switches, sockets, etc. (Point control boxes) shall be of 3 mm thick, fine finished PVC /Perspex materials and fixed to the enclosure in plumb with counter-sunk head, chromium plated brass screws. Outlets shall be terminated into a ceiling rose for fan points and into auto way porcelain or Bakelite connector for ceiling light points. For wall plug sockets, the conductors may be terminated directly into the switches and sockets. The outlets, points control boxes etc. shall be set out. Before fixing these, the contractor shall obtain clearance from the

O.O.W. with regard to their proper location. The enclosures of sockets and 3rd pin of the sockets shall be connected to the ground through a proper size earth continuity wires as laid out in standard specification.

## Luminaires General

The MCBs shall be rated for 9 KA fault level. The MCBs shall be checked & Coordinated with the down-stream MCBs for proper operation.

## Point Wiring

Point wiring shall commence from the first point control box / local control box for the points connected to the same circuit. Point wiring for, lights, fans, and 5A -15A sockets etc. shall be carried out with copper conductor PVC insulated wires of 1.0 & 1.5 Sq. m. Cross  section  as  per  BOQ.  The  points  wiring  shall  be  inclusive  of  40m  /  32mm  / 25mm/ 20mm PVC casing capping of standard and approved make (As specified

Here  in  before)  along  with  approved  quality  accessories  such  as  bends,  reducers, junction boxes, etc. together with wiring accessories such as ceiling roses, lamp holder, connector, points control boxes (enclosure for electrical accessories) etc. Points wiring shall be provided with 1.0mm copper conduit PVC insulated earth continuity wire for earthing 3rd pin of sockets, luminaries and fan fixtures. Light Control shall be either single, twin or multiple points controlled by a switch as specified.

## Testing & Electrical Installation

Testing and installation shall be as per IS: 7362-1963.

- The insulation resistance shall be measured by applying between earth and the whole system of conductors or any section thereof with all fuses in places and alai switches closed and except in earthen concentric wiring all lamps in position or both poles of the installation otherwise electrically connected together, where a direct current pressure of not less than twice the working pressure, provided that it need not exceed 500 Volts for medium voltage circuits. Where the supply is derived from the three wires (A.C. or D.C.) or a poly phase system, the neutral pole of which is connected to earth direct or through added resistance, the working pressure shall be deemed to be that which is maintained between the outer or phase conductor and the neutral.

- The insulation resistance measured as above shall not be less than 50 divided by the number of points on the circuits provided, that the whole installation shall be required to have an insulation resistance greater than one Meghan.

- Control rheostats, heating and power appliances and electric signs may, if required, be disconnected from the circuit during the test, but in event the insulation resistance between the case of frame work and all live parts of each rheostat appliance and sign shall not be less than that specified in the relevant

Indian standard specification or where there is no such specification shall not be less than half a mega ohm.

- The insulation resistance shall also be measured between all conductors connected to one pole or phase conductor of the supply and the entire conductor connected to the middle wire or the neutral or to the other pole or phase conductor of the supply and its value shall not be less than specified in sub clause (b).

- On completion of an electric installation (or an extension to an installation) a certificate shall be furnished by the Contractor countersigned by the qualified supervisor under whose direct supervision the installation was carried out. The certificate shall be in the prescribed form as required by the local electric supply authorities. One such recommended from is given in Appendix.

## Testing of Earth Continuity Path

The earth continuity conductor including metal conduits and metallic envelopes of all cases shall be tested for electric continuity and the electrical resistance of the same along with the earthing lead but excluding any added resistance or leakage circuit - breaker measured from the connection with the earth electrodes to any point in the earth continuity conductor in the completed installation shall not exceed one mega ohm.

## Testing of Polarity of Non-linked Single Pole switches.

- In two wires installation a test shall be made to verify that all no linked single pole switches have been fitted in the same conductor throughout and such conductor shall be labelled or marked for connection to an outer one phase conductor or to be the non- earthed conductor of the supply.

- In a three wire or four wire installation a test shall be made to verify that every non linked signal switch is fitted in a conductor which is labelled and marked for connection to one of the outer phase conductor of the supply.

## Certificate of Inspection

The contractor shall be responsible for getting the installation inspected and approved by the Electrical Inspector and other local electric supply authorities concerned, for getting the electric supply at the earliest.

The contractor shall obtain and deliver to the owners the certificate of final inspection and approved by the local electrical authorities concerned. The inspection fees etc. shall be paid by the, Contractor. In case any defects are pointed out by the Electrical

Inspector the contractor shall remove these defects at his own cost, and arrange for re inspection by the Electrical Inspector till such time the installation is finally approved and the required certificate is issued. The contractor shall bear all expenses and

deposit the necessary fees for the second and subsequent inspections by the Electrical Inspector.

## Additional specification and conditions

The contractor shall keep himself in touch with the building work and shall adjust his work accordingly so as to minimize breaking of masonry / concrete. No claim whatsoever on account of delay due to building work shall be entertained.

Any damage done to the building during the reaction of the work shall be made good by the contractor, free of charge to the satisfaction of the Engineer-In-charge. On his failure to do so the same will be made good at his risk and cost through another agency.

## Earthing:

Supplying & erecting funnel type earthing having earth plate of following size buried in specifically prepared earth pit 3 mtr. Below ground with 40 kg. charcoal and salt with alternate layers of charcoal & salt, 20mm dia. G.I. pipe with Funnel with a wire mesh for watering & bricks masonry block, C.I. cover complete as per Para 7.3 of IS 3043 with necessary length of double G.I. / copper earth wire No. 6 SWG bolted with lug to the plate and covered in 12mm dia. G.I. pipe 2.5 mtr. Long complete connected to the nearest switch gear with end socket as per direction & duly tested by earth tester confirming to ISS (As per drawing) with following specification.

# B. PROJECT SPECIFICATION

  - PIPE

## M.S. PIPE AND SPECIALS General

Pipe work including tapers, specials and bends shall be provided and completed. The pipes, and specials shall be of mild steel and fabricated to transmit flow without disturbing streamlined condition, too gradually and smoothly changes the direction or velocity as the case may be and to offer neat aesthetic appearance.

The M.S. pipes and specials to be provided by the contractor under this item includes on delivery, dished ends and specials.

Material and Fabrication

The pipes, specials and flanges shall be manufactured from mild steel plates generally conforming to IS: 226 Thickness of plates shall not be less than those stated below or nearest commercial thickness.

- M.S. pipes and specials 10 mm thick

- Dished end 20mm thick

## Mode of Measurement and Payment

The pipes and specials provided by the contractor such as pipes, specials flanges dished end and blank flanges are payable on Kg. - rate basis for complete work.

For calculation the weight for payment on rate per kg basis following parameters will be applicable.

- Wt. Of pipe and special shall be based on finished/fabricated component, Wastage will not be considered for payment.

- Thickness shall be average thickness of pipes supplied.	Iii) No deduction for bolt holes in flanges will be made.

- Nut bolts and washers will not be considered for weight calculation.

Specific weight of M.S. pipes and specials shall be assumed as 7850 kg. /Cum

- Cost of epoxy painting of M.S. pipes specials and valves are deemed to have been included in rate for Kg. Basis and shall not be considered separately for payment.

- Positive tolerance in the thickness of pipe is acceptable. The thickness shall be measured by ultrasonic gauge and it shall be measured by agency in presence of department Engineer at site with their instrument.

- Cost of breaking of pump house wall for pipeline work and making and finishing to original after completion of work is included in this item. Contractor should provide branch tees for air valve, pressure relief valve etc. Erected on manifold as per drawing and as per directions of Engineer-in-charge.

## Painting

For all M.S. pipes supplied by the contractor and manifold pipe the external surfaces of the pipe work and valves shall be painted with one coat of epoxy primer and two coats of epoxy paint approved by the Engineer. Painting shall be carried after completion of erection work.

The contractor shall test the pipe work for hydrostatic pressure. In presence of Engineer-in-charge. Charges towards this shall be borned by contractor

## M.S. fabrication

Providing, fabricating, erecting M.S. fabrication from ISMC / ISMB and other required size for base frame, pump supporting girder, for chain pulley block, and other required site situation. The payment will be made on weight basis.

## M.S. flanges

Providing,  fabricating,  erecting  M.S.  flanges  required  mm  dia.  20  mm  thick.   The flanges shall be machined on both sides. The flanges shall be welded to the M.S. pipes used for connecting the pumps and other accessories.  The payment will be made on weight basis.

## Flanged joints

The delivery of pump shall be connected to the rising main by making flanged joints required mm dia. To the MS pipes & specials. The flanges shall be jointed with fasteners of adequate strength and quality. The bolt diameters shall conform to IS:

1538.  The  joint  ring  between  flanges  shall  be  of  3mm  thick  rubber  of  adequate hardness for forming watertight joints and suitable to withstand pressure of required kg/Sq.cm. This item includes the cost of good quality rubber packing & nut bolts with washer. All flanged joints shall be hydraulically tested on full load of pump.

## Pressure gauge

This job covers providing and fixing as mentioned in BOQ mm dia. Glycerine filled pressure gauge Bourdon’s type pressure gauge as per IS 3624 : 1987 with brass cock, siphon tube, etc. As per direction of Engineer in charge. Contractor should provide suitable  tapped  holes  at  appropriate  places  for  fixing  these  pressure  gauges  &  the pressure  gauge  shall  be  located  at  a  height  of  2.5  feet  from  floor  level  to  ease  easy reading for the operator. The pressure gauges shall have range required Kg/ sq. Cm. Should be of approved make only.

## All cast iron specials Material

All Cast iron specials such as C.I. detachable joints shall confirm to I.S. 1538- 1993 (Part  1  to  24).  The  Supply  at  departmental  stores  shall  be  of  various  diameters  as specified. The specials shall be free from any defects. It should be possible to cut/drill the special to suit site condition to fit in the position. The hardness of the external surface shall not exceed 210 HBS. Rings shall confirm to IS 5382- 1985. Ring shall be homogeneous  and  free  from  porosity,  grit  and  surface  defects,  such  as  pitting, irregularities. Dimension of rings shall be as per IS 10292-1988.

## Manufacture:

The dimensions of flanged sockets and flanged spigots shall be as per Tables 7 & 8 of IS 1538-1993, respectively. Supply and Stacking at Departmental Store or Work Site: As specified under the agreement.

## Markings:

Each fitting shall have cast stamped or indelibly painted on it the following markings:

  - Manufacturer’s Name or trademark or identification mark.

  - The nominal diameter,

  - Mass of fitting,

  - Last 2 digits of year of manufacture,

  - Any other mark required by the purchaser.

Item to Include:

The item includes the supply of Cast Iron detachable joints, including all taxes, levies excluding octroi, transporting, loading, unloading and stacking at departmental store or work site as directed. The necessary test certificate also shall be provided along with the supply. Octroi paid shall be reimbursed on producing documentary evidence for the payment made.

## Mode of measurement and payment:

The item shall be measured as number of sets for the specified diameter of pipe. The rate shall be for supply of one number of detachable joint of specified diameter.

## D.I. PIPE

Supply and Delivery of Ductile Iron Pipe as per IS: 8329-2000 or its latest revision or amendments if any including jointing material as EPDM ring as per IS 5382-1985 and ISO: 4633-1996 or its latest revision or amendments if any

## Standards

The following standards, specifications and codes are part of this specification. In all cases, the latest revision of the including all applicable official amendments and revisions shall be referred to. In case of discrepancy between this specification and those referred to herein, this specification shall govern.

- ISO: 10803-1997 Design method for ductile iron pipes

- IS: 8329-2000 Centrifugally Cast (spun) ductile iron pressure pipes for water, gas and sewage

- ISO: 2531-1991 Ductile iron pipes, fittings and accessories for pressure pipelines.

- ISO: 4179-1985 ductile iron pipes for pressure and non-pressure-Centrifugal cement mortar lining – General requirements.

- IS: 8112 Specification for 43 Grade ordinary Portland cement.

- BS: 3416 Bitumen based coatings for cold application, suitable for use in contact with potable water.

- ISO: 8179-1995 ductile iron pipes-External coating-Part-1 Metallic Zinc with finishing layer.

- IS: 638 Sheet rubber jointing and rubber insertion jointing.

- ISO: 4633-1996 Rubber seals-Joint rings.

- IS: 5382-1985 Specification for Rubber sealing rings for gas mains, water mains and Waters.

- AWWA C600 Installation of ductile iron water mains and their appurtenances.

## Internal diameter

The nominal values of the internal diameters of pipe, expressed in millimetres are approximately equal to the number indicating their nominal sizes DN.

## Length

The working length of socket and spigot pipes shall be 5 m, 5.5 m, or 6 meters.

## Thickness

The wall thickness of pipe 'e' in mm shall be calculated as a function of the nominal diameter by the following equation with minimum of 5 mm

E = K (0.5 + 0.001 DN)

Where: e = wall thickness in mm, DN = the nominal diameter, K = the whole number coefficient

## EPDM Rubber Gasket

Rubber Gasket shall be suitably for Push-on-Joint.

The spigot ends shall be suitably chamfered or rounded off to facilitate smooth entry of pipe in the socket fitted with the rubber gasket

Rubber Gasket shall confirm to IS 5382-1985 and ISO: 4633-1996 its latest revision or amendments if any

## Sampling criteria

Sampling criteria for various tests, unless specified in IS 8329-2000, shall be as laid down in IS 11606. Mechanical test, Brinell hardness test, Hydrostatic test etc. Are shall be as per IS 8329-2000

## Tolerances on external diameter

The nominal external diameter (DE) of the spigot end of socket and spigot pipes and when   circumferentially   using   a   diameter   tape   measured   shall   confirm   to   the requirements specified as follow. The positive tolerance is +1 mm and applies to all thickness classes of pipes. The maximum negative tolerance of the external diameter is specified as follow

| DN | Nominal | Positive Tolerance | Negative Tolerance |
| --- | --- | --- | --- |
| 80 | 98 | +1 | -2.2 |
| 100 | 118 | +1 | -2.8 |

| DN | Nominal | Positive Tolerance | Negative Tolerance |
| --- | --- | --- | --- |
| 125 | 144 | +1 | -2.8 |
| 150 | 170 | +1 | -2.9 |
| 200 | 222 | +1 | -3 |
| 250 | 274 | +1 | -3.1 |
| 300 | 326 | +1 | -3.3 |
| 350 | 378 | +1 | -3.4 |
| 400 | 429 | +1 | -3.5 |
| 450 | 480 | +1 | -3.6 |
| 500 | 532 | +1 | -3.8 |
| 600 | 635 | +1 | -4 |

## Tolerance on Ovality

Pipes shall be as far as possible circular internally and externally. The tolerance for out-or-roundness of the socket and spigot ends is given below:

| Nominal Diameter in mm. | Allowable Difference between Axis and DE in mm |
| --- | --- |
| 80 to 300 | 1 |
| 350 to 600 | 1.75 |
| 700 | 2 |
| 750 to 800 | 2.4 |
| 900 to 1000 | 3.5 |

## Tolerance in thickness

The tolerance on wall thickness (e) and the flange thickness (b) of the pipes shall be as below:

| Dimensions | Tolerance in mm |
| --- | --- |
| Wall Thickness | -(1.3 + 0.001 DN) |
| Flange Thickness | +(2+0.05b) & - (2+0.05b) |

## Coating

Pipe shall be delivered internally and externally coated.

## External Coating:

Pipe shall be metallic zinc coated and after that it shall be given a finishing layer of bituminous paint as per IS - 8329-2000

| Nominal Pipe Size in (mm) | Nominal Lining Thickness |
| --- | --- |
| Up to 300 | 3 |
| 350-600 | 5 |
| 700-1200 | 6 |
| 1400-2000 | 9 |

Zinc coating shall comply with IS: 8329/EN 545/ ISO 8179. Only molten zinc spray coating shall be acceptable. The average mass of sprayed metal shall not be less than 130 g/sum. with a local minimum of 110 g/Sqm.

Bitumen  overcoat  shall  be  of  normal  thickness  of  70  microns  unless  otherwise specified. It shall be a cold applied compound complying with the requirements of BS 3416  Type  II  suitable  for  tropical  climates  factory  applied  preferably  through  an automatic process.

Damaged areas of coating shall be repainted on site after removing any remaining loose coating and wire brushing any rusted areas of pipe.

## Internal lining:

Internally pipe shall be Portland cement mortar lined (as per IS  - 8329-2000). The mortar shall contain by mass at least one part of cement to 3.5 part of sand.

All pipes and fittings shall be internally lined with cement mortar using high speed centrifugal process in accordance with IWO 4179/IS 8329. Cement mortar lining shall be applied at the pipe manufacturing shop in conformity with the aforesaid standards. No admixtures n the mortar shall be used without the approval of the Engineer. The quantity to cement proportion of sand if justified by the sieve analysis.

Pipe lining shall be inspected on site and any damage or defective areas shall be made good to the satisfaction of the Engineer.

Lining  shall  be uniform in  thickness  all  along the pipe.  The  minimum thickness  of factory applied cement mortar lining shall be as per IS: 8329 Annex-B or ISO 4179. This is given below.

Nominal Pipe Size (mm) Nominal lining thickness (mm) Up to 300 3 350-600 5 700-

1200 6 1400-20009

## Joint

Jointing of DI pipes and fittings shall be push-on type

## Push-on-joints

The   Contractor   shall   source   the   push-on-joint   gaskets   only   from   the   pipe manufactures.  In  turn  the  pipe  manufacturer  shall  supply  at  least  10%  additional quantity of gaskets over and above the requirement to the Contractor at no extra cost.

The gasket used for joints shall be suitable for natural and purified water conveyance. In jointing DI pipes and fittings, the Contractor shall take into account the manufacturer’s recommendations as to the methods and equipment’s to be used in assembling the joints. In particular the Contractor shall ensure that the spigot end of the pipe to be jointed is smooth and has been properly chamfered, so that once the rubber ring is correctly positioned before the joint is made, does not get damaged by friction or sharp edges of the spigot Chamfer. The rubber rings and the recommend lubricant shall be obtained only through the pipe manufacturer.

Rubber ring bundles form every lot shall carry with them manufacturers test certificate for the following mechanical properties.

## Hardness

  - Tensile strength 2. Compression set 3. Accelerated again test 4. Water absorption test 5. Stress relaxation test Rubber rings shall be clearly labelled in bundles to indicate the type of ring, the type of joint, the size of the pipe with which they are to be used, the manufacturer’s name and trade mark, the month and year of manufacture and the shelf life.

## Testing of pipe:

The main test among others to be conducted shall be as per IS: 8329-2000 or with its latest revision/ amendments.

## Mechanical Tests

Mechanical tests shall be carried out during manufacture of pipes as specified in the Standards.  The  frequency  and  sampling  of  tests  for  each  batch  of  pipes  shall  be  in accordance  with  IS  11606-1986.  The  test  results  so  obtained  for  all  the  pipes  and fittings of different sizes shall be submitted to Engineer. The method for tensile tests and the minimum tensile strength requirement for pipes and fittings shall be as per IS; 8329/EN 545 for pipes and IS: 9523/EN 545 for fittings.

## Brinell Hardness Test

For checking the Brielle hardness the test shall be carried out on the test ring or bars cut from the pipes used for the ring test and tensile test in accordance with IS:1500. The test shall comply with the requirements specified in IS: 1500/ISO 6506.

## Re-tests

If any test piece representing a lot fails in the first instance, two additional tests shall be made on test pieces selected from two other pipes from the same lot. If both the test results satisfy the specified requirements the lot shall be accepted. Should either of these additional test pieces fall to pass the test, the lot shall be liable for rejection.

- For hydrostatic test at works, the pipes and fittings shall be kept under test pressure as specified in the standard for a period of minimum 15 seconds during which the pipes shall be struck moderately with a 700 g hammer for conformation of satisfactory sound. They shall withstand the pressure test without showing any leakage, sweating or other defect of any kind. The hydrostatic test shall be conducted before surface coating and lining.

## Quality Assurance

The manufacturer shall have a laid down Quality Assurance Plan for the manufacture of the products offered which shall be submitted along with the tenders. DI Specials with all types of diameters suitable of K9-K7 grade pipes with inner cement mortal lining

The necessary DI Specials required during the lowering & lying of Ductile Iron Pipe shall be supplied by the agency and shall be as per standard specification. And per IS specification

It shall be of best quality as per requirement Rate shall be including loading, unloading, carting, insurance and labour charge etc. Complete.

The payment shall be made on kg. Basis.

M S Specials of required thickness with 3 coats of approved make epoxy paint with inside and outside

The necessary MS Specials required during the lowering & lying of MS/AC/DI & PVC Pipe shall be supplied by the agency and shall be as per standard specification.

MS specials included Air valves risers, Flanges, Tailpiece etc.

It shall be of best quality as per requirement Rate shall be including loading, unloading, carting, insurance etc. Complete.

## Mode of Measurement and Payments

The payment shall be made as mentioned in price bid.

The measurement shall be taken in running meter of the pipes. The payment shall be made on running meter base. Item includes all taxes, octroi, insurance, transportation, freight charges, loading, unloading, conveyance to site, staking etc. Including necessary testing charges. Lowering, laying and joining DI K-7/9 pipes of various classes with ISI specials of following diameters in proper position grade and alignment as directed by engineer - in- charge including conveyance.

## General:

The pipes & joints shall be procured, supplied by the Contractor at work site at his own cost. Every care shall be taken in carting them to site. During transportation any damage shall be occurring to pipes for fittings the replacement of pipes given by the contractor at his own cost.

The trenches shall be well levelled so that pipes are laid evenly among them. The pipes shall be fixed within two rubber rings to be supplied by department at the place shown in schedule A, if directed by the Engineer-in-charge or mentioned in item of schedule

- The specification for titan joints i.e. Rubber Rings shall be as per details specification material section Item No-37.

The contractor shall make his own arrangement for obtaining permission for storing & stacking of pipes etc. From land boards whether they are Government, Municipal Local Bodies or Private land owner.

Every pipes before lowering into the trenches shall be got checked and thoroughly cleaned and the beds of the trenches shall be properly graded and levelled as required on the line, without any claim for extra cost whether it is required. The pipe shall be carefully lowered into the trenches with the help of a suitable type of chain pulley blocks, which shall first be approved by the Engineer-in-Charge. Each pipe shall be properly jacked and the spigot perfectly fixed into the socket. No jointing operation shall be started unless the gradients levels are approved by the Engineer-in-Charge or his representatives.

The pipes shall be laid complete in centreline ranged accurately by means of a string attached to both marked centre of site rails and no deviation shall be permissible without the permission of Engineer-in-Charge. The pipe shall be laid in reasonably dry trenches and no circumstances on slushy bedding.

The pipes shall be brushed before lowering any lying or remove any soil or dirt etc. That may have accumulated.

The inside socket and outside of the spigot-shall be carefully cleaned. The pipe shall be lowered carefully with socket and toward and the flow of water or up till or as directed and spigot and should be carefully inserted into the socket and the space shall be filled with the joint.

DI specials shall be conforming to IS 9523-2000 and flanges shall be of PN-10 class.

## Notes:

  - If any damage is caused to the pipeline during the execution of work or while cleaning / testing the pipeline as specified, contractor shall be held responsible for the same and shall replace the damaged pipeline and retest the same at his own cost to the full satisfaction of Owner / Engineer In-Charge.

  - After for testing of pipeline shall be arranged by contractor at his own cost.

  - Balance 5% will be released on flow testing & satisfactory completion of the section.

  - Additional 5% will be released on completion of satisfactory flow test, cleaning of pipeline, commissioning the section. 5 Kms of Un laid length of pipe in irrespective of diameter shall be paid at a time and other pipes should be paid after laying only

## D.I. Specials

DI Specials with all types of diameters suitable of K9 grade pipes with inner cement mortal lining. The necessary DI Specials required during the lowering & lying of Ductile Iron Pipe shall be supplied by the agency and shall be as per standard specification. And per IS specification

It shall be of best quality as per requirement Rate shall be including loading, unloading, carting, insurance and labour charge etc. Complete

## HDPE PIPES

The specifications for HDPE pipes of various diameters are confirming to I.S.4984 – 1995.

## Grade of Raw Material

Raw  material  used  to  manufacture  the  HDPE  pipes  shall  be  pre  compounded  at manufacturing stage. PE 100 is resin proposed to be used for  manufacturing of the pipes.

## General:-

- The material used for the manufacturer of pipe should not constitute toxic hazard, should not support microbial growth and should not give rise to unpleasant taste and odour or discoloration of water. Pipe manufacturer shall obtain a certificate to this effect from the manufacturer of raw material.

- High density polyethylene (HDPE) used for the manufacture to designation PEEWA

– 45 – T – 006 of IS 7328: 1992. HDPE conforming PEEWA – 45 – T012 of IS 7328:

1992 may also be used with exception that met flow rating (MTR) shall not exceed 1.10 g/10 minutes – In addition the material shall also conform to 5.6.2 of IS 7328: 1992.

- The specified base density shall be 946.5 Kg/m³ and 946.4 Kg/m³ (Both inclusive) when determined at 270 C according to procedure prescribed in IS 7328: 1992.The value of the density shall also not differ than 3 Kg/m³

- The melting flow rating (MFR) shall be between 0.41 and 1.10 (both inclusive) when tested at 1900 C with nominal load of 5 Kg & as determined by method prescribed in 7 of IS 2530 : 1963. The MFR of the material shall also be within 20% of the value declared by the manufacturer.

- The resin shall be compounded with carbon black. The carbon black content in the material shall be within 2.5 0.5% and dispersion of carbon black shall be satisfactory when tested according to the procedure described in IS 2530: 1963.

- The percentage of the antioxidant used shall not be more than 0.3 percent by mass of finished resin.

## Quality Assurance Certificate

Quality assurance certificate for the raw material proposed to be used for the project, from one of the certifying agencies such as Body coat or Slevan or Advantica or any other internationally reputed organization shall be submitted along with the supply.

The  manufacturer  should  submit  the  above  raw  material  certificates  for  proposed grade of material PE – 100 at time of supply of pipe.

Contractor shall submit the following Certificates from the manufacturer.

## Pressure Rating

The pressure rating of HDPE pipes and specials shall be confirming to I.S. 4984-1995 for 6 Kg/cm² (working pressure) for material grade PE 100.

## Colour of pipes

The Colour of the HDPE pipe shall be as specified in IS code is black. The pipe shall be designed for the temperature of 450 C maximum.

## Reworked material.

The addition not more than 10% of the manufacturer’s own rework material resulting from the manufacturer of pipes is only permissible.

## Dimensions

The pipe dimensions shall be as per latest revisions and amendment of  specified in standards IS 4984-1995. The pipes shall be supplied in straight lengths of 20 m. Short length of 3 m (Min) up to maximum of 10% of total supply will be permitted.

The internal diameter, wall thickness, length and other dimensions of pipes shall be as per relevant clauses given in IS 4984 applicable, for different class of pipes. Each pipe shall be of uniform thickness throughout its length.

The dimension to tolerances shall be as per specified I.S. standards.

## Performance requirements

The pipe supplied should have passed the acceptance tests as per clause given in specified IS standards. The manufacturer should provide the test certificates for the tests conducted, as required in specified standards along with the supply of pipes.

These  acceptance  tests  can  be  performed  in  the  in  house  laboratory  of  the  pipe manufacturing  factory  of  the  successful  Contractor.  Third  party  inspection  shall  be carried   from   1)   M/s   Central   Institute   of   Plastic   Engineering   &   Technology, Aurangabad.  2)  M/s  Dr.  Amin  Controler  Pvt.Ltd,  Mumbai  3)  M/s  WAPCOS  Ltd., Gandhi Nagar shall have to submit to Department / Grampanchyat, after supply of pipe at site. Then only it can be measured and recommended for further payment.

## Marking

As per the provisions of clause given in specified standards each straight length of the pipe shall be clearly marked in inedible ink/paint the following information shall be marked.

  - ISI stamping with marking of IS 4984(or IS 14333)

  - The manufacturer’s name and /trade mark.

  - Designation of the pipe as per IS 4984 (or 14333)

  - Lot number /Batch number

## BIS License

The pipe manufacturer who is going to supply the pipes for the project has to have a valid BIS license.

## Bid without these licenses may be treated as non-responsive Fittings/Specials

All HDPE fittings/specials shall be fabricated in accordance with IS: 8360 (Part I & III). PE Injection moulded fittings shall be in accordance with IS: 8008 (Part I to IX). All fittings /specials shall be fabricated or injection moulded at factory only. No fabrication or moulding will be allowed at site, unless specifically permitted by the Engineer.

Fittings will be butt welded on to the pipes or other fittings by use of heat fusion.

## Bends

HDPE Bends shall be plain square ended as per IS: 8360 part I & III specifications. Bend may be moulded shall be manufactured or fabricated from pipes elements.

## Tees

HDPE Tees shall be plain square ended as per IS: 8360 Part I & II specifications. Tees may be equal tees or reduced bench off tees. Tees may be moulded or fabricated from pipes elements.

## Reducers

HDPE Reducers shall be plain square ended as per IS: 8008 Part - I & VII Specifications.

## Flanged HDPE Pipe Ends.

HDPE Stub ends shall be square ended as per IS: 8008 Part & VII Specifications. Stub ends will be welded on the pipe. Flange will be of slip on flange type as described below.

## Slip on Flanged

Slip-on-flanges shall be metallic flanges covered by epoxy coating or plastic powder coating.  Slip  on  flanges  shall  be  conforming  to  standard  mating  relevant  flange  of valves, pipes etc. Nominal pressure rating of flanges will be PN 10.

## Welding Procedure

Jointing between HDPE pipes and specials shall be done as per the latest IS: 7634 Part

- Method of jointing between the pipes to pipes and pipes to specials shall be with butt fusion welding using semi-automatic, hydraulically operated, superior quality butt fusion machines which will ensure good quality butt fusion welding of HDPE pipes.

Normally butt fusion welding shall include following activities.

  - Alignment of pipe on welding M/C

  - Surface preparation for welding.

  - Heating of pipe ends

  - Holding pipe ends for welding

  - Cooling etc.

## Installation and Commissioning of HDPE PIPES Installation

- Supplying, laying, jointing, testing and commissioning of pipes shall conform to relevant IS codes, as applicable.

- The alignment of pipelines shown in drawings of the tender documents is only indicative and the exact alignment will be as per drawings and /or as directed by the Engineer or his representative.

- The HDPE pipes shall be laid in accordance with the latest IS 7634 Part -2.

## Hydraulic Testing of HDPE Pipe Line

- The Sectional Hydraulic Test shall be carried out after the pipeline section to be tested has been laid jointed and backfilled to a depth sufficient to prevent floatation.

- Each length of the pipeline to be tested shall be capped or blanked off at each end and securely strutted or restrained to withstand the forces which will be exerted when the test pressure is applied.

- Proposals for testing where thrusts on structures are involved even where thrust flanges on the piping are installed, shall be with the prior approval of the Engineer.

- The proper method of filling the pipeline with water shall be used. The length under test shall be filled making certain that all air is displaced through an air valve or any other appropriate mechanism. The test length shall then remain under constant moderate pressure as per testing method given in the IS 7634.

- As per IS code water required to build up allowable drop in pressure during test will be treated as a makeup water.

- Notwithstanding the satisfactory completion of the hydraulic test, if there is any discernible leakage of water from any pipe or joint, the Contractor shall, have to be repaired at his own cost, replace the pipe or repair the pipe or remake the joint and repeat the hydraulic test is the responsibility of the contractor. The additional payment will not be made.

- Test pressures are to be measured in kg/cm² at the centre of the bank flange situated at the lowest end of the pipeline under test.

HDPE Pipes and Fittings:

All the pipes specials and fitting of HDPE shall be supplied and shall be tested along pipeline as per relevant IS codes and specifications.

Daily O & M of HDPE pipeline should be done & maintain by contractor for two years free of cost. No extra payment will be done by MJP for this.

## The Following code shall be used for:

- Site Test Pressure: as per IS 7634 Part I.

Suitable section length shall be 500 to 800 m as directed by the Engineer in charge shall be taken for such testing from time to time during progress of the work and satisfactory test given for that section. All testing apparatus, gauges, connections, etc. And water required for testing shall be arranged by the Contractor at his cost. The MJP does not undertake any responsibility to supply water for testing, If there is delay in testing, the contractor shall refill the trenches for the time being and reopen them at time of testing at his own cost, failure of which shall entitle the MJP to do the refilling the reopening of trenches at the risk and cost of the contractor. If the trenches are filled due to any reason whatsoever before testing the contractor shall have to open for testing at no extra cost.

Satisfactory  hydraulic  test  shall  be  recorded  when  the  section  under  test  shall withstand the pressure as specified by the Engineer in charge for about 15 minutes without operating the test pump. The test pressure being maintained at the specified figures during that 15 minutes interval.

The field pressure to be imposed should be not less than the maximum of following

  - 1.5 times the maximum sustained operating pressure.

  - 1.5 times the maximum static pressure in the pipe line.

  - Sum of maximum sustained operating pressure and maximum surge pressure.

  - Sum of maximum pipe line static pressure and maximum surge pressure. Subject to the maximum equal to the work test pressure to any pipe fitting incorporated.

  - The field test pressure should wherever possible be not less than 2/3 rd. work test pressure and should be applied and maintained for at least 15 minutes.

The test pressure shall be gradually raised at the rate of 1 Kg/ cm2/min. If the pressure measurement are not made at the lowest point of the section, an allowance should be made  for  the  difference  in  static  head  between  the  lowest  point  and  point  of measurement  to  ensure  that  the  maximum  pressure  is  not  exceeded  at  the  lowest

point. If a drop in pressure occurs, the quantity of water added in order to re-establish the test pressure should be carefully measured. This should not exceed 0.1 lit/ mm of pipe dia. Per Km. Of pipeline per day for each 30 cm. Head of pressure applied.

During testing if any joints are found leaking they shall be repaired and /or redone by the contractor at his cost till the test is found satisfactory. Similarly, any pipes, collars, specials, show hair cracks, leaks etc. During testing the contractor shall replace them with sound pipes and specials etc. Free of cost. The hydraulic test shall be given in presence of the Engineer in charge.

15% payment of total sub work of pipe line work shall be withheld till hydraulic test is given which shall be released only on giving satisfactory test.

## Mode of Payment:

60% payment shall be released against providing HDPE pipes, after submitting third party  inspection  certificate  from  1)  M/s  Central  Institute  of  Plastic  Engineering  & Technology,  Aurangabad.  2)  M/s  Dr.  Amin  Controler  Pvt.Ltd,  Mumbai  3)  M/s WAPCOS  Ltd.,  Gandhi  Nagar  25%  payment  will  be  made  after  lowering,  laying, jointing of pipes. 15% payment will be released after satisfactory hydraulic testing is given by contractor. The cost all types specials required as per site conditions is on Lum-Sum basis.

# 2. VALVES

## Sluice Valve (Glandless) with Actuator

The entire assembly comprising valve actuator reduction gear box and head stock shall be supplied by the approved valve manufacturer only and documentary proof for the same shall be submitted.

## Sluice valve

Providing, erecting and commissioning of all types of dia. Sluice Valves without bypass shall be of approved by the Executive Engineer and shall be provided in the delivery pipe of each pump. The sluice valves of cast iron body suitable for the PN- of all Rating shall be provided and shall confirm to relevant IS6. The   sluice valves shall be double flange, water works pattern, inside  screw, non-rising spindle type and shall be fitted with double faced gunmetal taper wedge made in one piece and having two machined facing rings securely fixed into machine recesses in the wedge. The guides and the lugs shall be provided to guide the wedge through its full travel and the lugs and guides shall  be  lined  with  bronze.  The  bronze  liners  provided  on  guides  and  lugs  shall  be secured by counter sunk screws or rivets of nonferrous metals. The clearances (radial and lugs axial) between the lugs and guides shall not exceed 2.5mm. All valves shall be provided on delivery side of pump.

| MATERIALS OF CONSTRUCTIONS: |  |
| --- | --- |
| Body, bonnet cover and wedges | Grey cast iron |
| Stuffing box and gland. | FG – 200 of IS-210 |
| Spindle | Stainless steel IS:6603 |
| Wedge and body rings | Leaded in bronze conforming to grade-2 of IS:318 |
| Nuts and Bolts | As per IS: 1363 |
| Wedge Nut | High tensile brass conforming to Alloy 3 of IS : 320 |

## Sluice Valve (Glandless)

Class 300, Cast Steel sluice valve shall be provided on the delivery pipe of each pump. The valve shall be double flanged water works pattern inside screw with non-rising

spindle. The valve shall generally conform to Class 300 rating of relevant international standard. The valve shall be suitable for operation with valve actuator mounted on valve body with reduction gear box and head stock.

The materials of construction shall be as per relevant standard with stainless steel spindle of grade specified in standard. Thrust bearing shall be located in suitable housing above stuffing box and shall be oil/grease lubricated. Construction shall be such that ingress of water into bearing housing is totally prevented.

The valve shall be subjected to test at manufacturer’s works in the presence of the Third Party Engineer for seat and body test at the pressure stipulated for the rating and entire operation with valve actuator simulating field installations.

## Material of construction of Valve

Body, Bonnet - CS ASTM A216 Gr WCB

Body Seat Ring - SS CA15 / CS WCB +13% Cr. HF Wedge - CS WCB +13% Cr. HF

Spindle & Gland Bush - SS AISI type 410 Seal (O) ring – Nitrile rubber

Back Seat Bush - SS AISI type 410 Yoke Sleeve - SG Iron / Gun Metal

Gasket - Spiral wound SS 304 + Graphoil filled Body Studs - ASTM A 193 Gr B7

Body Bolts - ASTM A 194 Gr 2H

Ends - Flanged Drilled to ANSI B16.5, CL-300

## Valve Actuator

Electromechanical valve actuator shall be provided for sluice valve of individual pump delivery line the actuator shall be electrically operated. However features shall be incorporated to disengage electric motor and operate the actuators manually.

## Actuators

The actuator shall be designed to open and close with manual push button operation considering actual torque required for opening and closing of actuator and under shut off condition.  The operating speed shall be designed for valve stroke of approximate 250 mm per minute during valve closing and opening operation.  The enclosure shall be   fully   weatherproof   it   shall   incorporate   double   ‘O’   sealing   arrangement   for protection  of  electrical  component  from  moisture  and  dust  at  all-time  even  when terminal  covers  are  removed,  mechanical  indicator  for  sluice  valve  close  and  open should  be  provided  on  actuator.  The  actuator  shall  also  incorporate  hammer  blow feature to open the valve.

## Motor

The electric motor shall be 3 phase squirrel cage, Class-B insulated with a time rating of 10 minutes or twice the valve stroking time, whichever is longer.  The HP of motor shall be with extra margin.

## Drive

The actuator gear box shall be of the totally closed oil/greased lubricated type the arrangement shall be such that the gear case can be opened for inspection or disassembled without taking the valve out of the service.

The drive shall incorporate bottom entry drive bushing which shall be easily detachable and machined to fit on valve spindle.

## Manual operation

A hand wheel shall be provided at appropriate level for manual operation. The mechanism shall be such that the manual operation is possible only when motor is disengaged by means of lever.

## Limit switches

Limit switches shall be provided for open and close torque and/or positions. Means shall be provided to prevent the open torque switch tripping during initial unseating hammer blow effect.

All required electrical and mechanical connections including power and control cables shall be provided and cost of all such items shall be deemed to be included in the quoted cost for valve and actuator.

Necessary support in CC block shall be provided underneath the valve.  If required CC platform  shall  be  provided  to  ensure  that  height  of  hand  wheel  is  1  m  above  the platform cost of CC support and platform shall be separately under relevant item in Schedule-B.

## Testing

All the Sluice valves & Valve actuators shall be subject to factory test in Presence of Superintending Engineer (M) or his representative and third party. Inspection agency approved by MJP.

The scope of third party inspection by the agency approved by MJP is as under for all Sluice valves:

Review of raw material test certificate and quality control procedure.

    - Body and seat test

    - Test with operation of actuator and reduction gearbox fully assembled with valve opening and closing with synchronizing.

    - Checking wear travel.

## For Valve Actuator:

      - Review of raw material test certificate and quality control procedure.

      - High voltage test

      - Insulation resistance test

      - Checking wiring diagram and circuit

Acceptable makes: As per Mechanical approved list of MJP.

## Reflux valve

All type of dia non-return valve generally conforming to relevant international standard shall be provided on the delivery pipe of each pump. The valve shall have free acting, quick opening, non-slam closure, and low head loss characteristics. The entire assembly shall be suitable for all working pressure and also body test pressure of construction materials shall be as per relevant standard. However, rubber faces

shall not be offered. Non-Return valve shall be multidoor generally conforming to relevant standard and shall be installed on rising main at location as directed by Engineer in Charge. Alternatively CIDF valve with sliding disk generally as per construction of zero velocity valve can be accepted if manufacturer and contractor jointly give guarantees. The NRV/ZVV shall be provided on rising main.

The valves shall be of approved make and shall be tested at manufacturer’s works for seat and test and body test for test pressure in presence of the Third party inspection agency.

| MATERIALS OF CONSTRUCTIONS: |  |
| --- | --- |
| Body, cover, door and door face disc. | Grey cast iron confirming to grade |
| Disc. | FG –200 of IS-210 |
| Hinges | Cast steel to IS:1030 |
| Hinges pins, door pins & door | Stainless steel to IS:6603 |
| Suspension pins |  |
| Bearing bushes, body hinges and | Gun metal conforming to grade 2 |
| Door faces | of IS:318 |

## Testing

All the Reflux valves shall be subject to factory test in presence of Superintending Engineer (M) or his representative and third party inspection agency approved by MJP.

The scope of third party inspection by the agency approved by MJP is as under

        - Review of raw material test certificate and quality control procedure.

        - Body test and seat test.

All test certificates in triplicate shall be submitted along with supply of valves.

## Acceptable makes:

As per approved mechanical list of MJP

Cast Steel Reflux valve (class 150/300)

Non-return  valve  generally  conforming  to  relevant  international  standard  shall  be provided on the delivery pipe of each pump.   The valve shall have free acting, quick opening, non-slam  closure, and low  head  loss characteristics.   The entire  assembly shall be suitable for working pressure of 52 Kg/Sq. cm. and body test pressure of 78 Kg/Sq. cm construction materials shall be as per relevant standard.  However, rubber faces shall not be offered.  Non-Return valve shall be multi door generally conforming to relevant standard and shall be installed on rising main at location as directed by Engineer in Charge. Alternatively M.S. fabricated valve with sliding disk generally as per construction of zero velocity valve can be accepted if manufacturer and contractor jointly give guarantee for 3 years.  The NRV/ZVV shall be provided on rising main.

The valves shall be of approved make and shall be tested at manufacturer’s works for seat and test and body test for test pressure in presence of the Third party inspection agency.

Necessary CC support shall be provided underneath the valves and shall be paid under relevant item in Schedule ‘B’.

## Material of Construction

Reflux Valve:

          - Body, Cover & Hinge - CS ASTM A216 Gr.WCB

          - Disc - CS WCB + 13% Cr. HF

          - Body Seat Ring- SS CA15 / CS WCB +13% Cr. HF

          - Washer, Hinge Pin & Split Nut - SS AISI 410

          - Gasket - Spiral Wound SS 304 + Graphoil filled

          - Cover Stud / Nut - ASTM A 193 Gr B7 / A 194 Gr 2H

          - Valves 400mm & above sizes are with Counter weight arrangement.

          - Ends- Flanged Drilled to ANSI B16.5, CL-300

## Testing

All the Reflux valves shall be subject to factory test in presence of Superintending Engineer (M) or his representative and third party inspection agency approved by MJP.

The scope of third party inspection by the agency approved by MJP is as under

- Review of raw material test certificate and quality control procedure.

- Body test and seat test.

All test certificates in triplicate shall be submitted along with supply of valves.

Acceptable makes:	As per approved mechanical list of MJP

Butterfly Valve

Butterfly valve shall  be short  wall  body  pattern conforming  to BS  5155 suitable for working pressure and body pressure. The manual actuator with suitable hand wheel shall be provided to operate the valve.  The shaft shall be horizontal. The dia. Butterfly valve shall be installed on rising main as directed by Engineer-in-Charge.

The valve seat of the disc shall be synthetic rubber and renewable without dismantling the valve. All fasteners shall be stainless steel. The casting shall conform by third party inspection agency. Necessary CC support shall be provided underneath the valve and shall be paid separately under relevant item in Schedule-B.

## Testing

All the valves shall be subject to factory test in presence of Superintending Engineer

(M) or his representative and third party inspection agency approved by MJP. The scope of third party inspection by the agency approved by MJP is as under

- Review of raw material test certificate and quality control procedure.

- Body and seat test.

Acceptable makes:	As per Mechanical approved list of MJP.

Kinetic Air Valve

Double orifice kinetic type dia air valve of approved make by MJP shall be provided on 800 mm dia common manifold as shown in drawing as per direction of Engineer-in- Charge. The air valve shall be suitable for working pressure and isolating sluice valve designed for working pressure of shall be provided.

The air valve shall be mounted on dia branch hole with taper of size and at height. The air valve shall be of approved make by MJP only and shall be test at factory in presence of Third Party Inspection agency approved by MJP.

## Testing

All the valves shall be subject to factory test in presence of Superintending Engineer (M) or his representative and third party inspection agency approved By MJP.

The scope of third party inspection by the agency approved by MJP is as under

  - Review of raw material test certificate and quality control procedure.

  - Body and seat test.

  - Operation test for functioning of small orifice and large orifice.

Acceptable makes: As per Mechanical approved list of MJP.

## M.S. dismantling Joints.

A dismantling joint  shall  be provided between the discharge  elbow  and non-return valve  in  delivery  line  of  each  pump  &  dismantling  joint  shall  be  provided  between butterfly valve & N.R.V. for easy assembling and dismantling of the pipe work.   The shell  thickness  shall  be  10  mm.  The  dismantling  joint  shall  be  withstanding  test pressure or twice the shut off whichever is greater.  The design shall generally confirm to typical drawing of dismantling joint.  The tenderer may offer other technically equal arrangement.  The arrangement shall however fully ensure that…

  - When assembled and under dynamic load the bolts together shall withstand pull equal to 1.5 times the duty head and no torque or pull is extend on the pump foundation arrangement.

  - During assembling or dismantling the sliding flange can be slide adequately to enable to detach the discharge tapper and piping from each other.

  - The seal ring joint shall be designed to withstand test pressure and without any leakage

  - The sliding flange should slide at least 20 mm.

## Testing

The scope of third party inspection of the dismantling joints by the agency approved y MJP and Superintending Engineer (Mech.) or his representative is as under:

- Review of raw material test certificate and quality control procedure.

- Operation test.

# EXCAVATION

## General

The  specifications  contained  in  the  standard  specification  volume  2nd  published  by public works and housing department, govt. Of Maharashtra, chapter shall apply.  In addition  to  above  following  specification  shall  apply.    In  case  of  any  discrepancy between the two the below given specifications shall govern.

## Site clearance

The area to be excavated shall be cleared off. All trees and bushes and rubbish and other objectionable materials removed shall be burnt or disposed off as directed by the engineer-in-charge. The cost of such clearing shall be deemed to have been included in the rates accepted for different items under excavation.

## Dewatering

No distinction shall be made as to whether the materials being excavated is dry, moist or wet. The item also includes bailing out of water by manually or pumps to keep the trenches reasonable dry for all further works of lowering, laying, jointing and testing of the pipe line till the completion of the work.

## Shoring and strutting

The item includes all shoring and strutting that may be required. On no account the width of trenches more than these mentioned here in after shall be measured. If excavation width more than the specified is required for the purpose of keeping machinery, steeping due to loose material or for any other reasons the same shall be at the contractors cost.

## Lighting, barricading and guarding

The items of excavation are including necessary lighting at night at suitable intervals, but  not  more  than  15  meter  along  the  excavated  trenches  and  at  all  crossing  and barricading  the  same  by  fencing  so  as  to  avoid  the  accident.   Chowkidars  shall  be employed at place where the trenches cross over any traffic road to caution the vehicles and pedestrians etc. The arrangements shall be maintained till completion of work and at the cost of the contractor.

## Alignment and levels

Before the trenches excavation is commenced, sight rails shall be erected at every 30 meters and at all points of change of direction, gradient and at ends. The excavation work shall be preceded by a detailed survey along the alignment of the main to obtain ground levels at every 30 meters or less distance. Temporary bench mark shall be constructed at every 30 meters distance along the alignment and shall be maintained till the completion of work. All labour and materials required for the survey work of fixing bench mark etc. Shall be provided by the contractor at his own cost. For any mistakes in survey the contractor is fully responsible. He should not lay the pipes, unless the alignment is thoroughly checked by the engineer-in-charge or his authorized representative who is empowered to sign the work order book in token of checking the exact grade and level of the trenches excavation.

Excavation at random places shall not be measured by the MJP's engineer. Any non- technical practices during the excavation of the contracted work shall be viewed very seriously by the MJP and a note to that effect will be recorded against the contractor in his name.

## Depth and grades of trenches

The trenches shall be excavated to the required grades and depth in all types of strata and on the lines as shown on approved drawings or as directed by the engineer-in- charge, if not so, the payment for the item will not be paid to the contractor. The depth of excavation and the levels of the pipe inverts shall be checked by means of boning rods of suitable lengths. Additional depths if required to be excavated for pipes, for sockets, collars, specials, joints and for any other working facility and shall not be measured and paid. The minimum cover above the pipe shall be 0.90 m.

The contractor shall notify the engineer when the trenches are ready for bedding so that the engineer can inspect and record the depth. Only on explicit approval by engineer, the bedding shall be provided by the contractor. If any public utility i.e. electrical cable, telephone cable, water connections, sewer connections, gutter damage etc. Then same will be rectified by contractor at his own cost.

## Pressing and consolidating of the trenches

The bed of the trenches shall be well rammed before laying of the murum or sand for bedding hollows, if any, shall be filled with murum duly rammed and watered to required level and grade at cost of the contractor.

## Classification of materials in trenches

The exact classification of the strata met with during the excavation shall be done by the representative of engineer-in-charge and accordingly measurement shall be recorded under different items of excavation provided under annexure to clause-38 of tender for the purpose of excess quantity. In case of any, dispute regarding classification of strata, the decision of engineer-in-charge shall be final and binding. The strata classifications and its quantity shown are indicative only. The contractor therefore, shall carry out his own assessment regarding the strata at different depth along the alignment, before submission of the tender.

## Excavation by chiselling mechanical means (in hard strata)

Excavation in hard strata shall be done by chiselling, wedging or line drilling as specified any mechanical all means or ordered by the engineer. The excavation refers to excavation generally for foundation, wet or dry, in hard rock by chiselling, wedging or line drilling and shall comply with the specifications.

## Mode of measurement and payment

The excavation shall be measured in cubic meters only. Dimensions shall be measured correct to two decimal of meter and quantity shall be calculated to two places of decimal of cubic meters. The item mentioned in schedule-b in which includes disposing excess excavated material remained after refilling will not be paid separately for disposing excavated material.

# B.B. MASONRY CHAMBER

The work is to be carried out as per type design or drawing of the department and as per detailed description of the item in Schedule-B of the tender. Sizes of chamber mentioned in the item are the clear internal dimensions of the chamber after completion of plastering. Unless otherwise mentioned in the wording of item in Schedule-B of the tender the rate for this item shall include following allied works.

  - The cost of extra excavation in all types of strata which is in addition to the line trench, refilling the sides and disposing off surplus stuff will be paid separately under relevant item.

Excavation covered by pipe line trenches coming under M.H. chamber shall not be admissible for payment.

  - Providing and casting at site 15 cm thick bed concrete in CC M-100 below external size of complete chamber.

  - Providing B.B. masonry side walls in 225 mm thick in CM 1:5

  - Providing 20 mm thick plaster in CM 1:3 from inside.

  - Providing cement plaster 20 mm thick in CM 1:3 from outside at least up to 30 cm below ground level.

  - Providing top coping 15 cm thick in M-150 with smooth finishing to surface.

  - Providing and fixing in position pre-cast RCC manhole frame cover.

  - Unless otherwise directed by the department the finished top of the chamber constructed on road surface and shall not cause hindrance to traffic.

## Mode of Measurement

This item will be measured and paid as per number basis.

# REFILLING OF TRENCHES OF PIPELINE

After lowering, laying, jointing and welding of pipe line, site gunitting and concreting work, refilling of trenches with available excavated stuff shall be done.

The available excavated stuff shall be laid in layers of 15 cm to 20 cm. Each layer shall be  watered  and  compacted  before  the  upper  layer  is  laid  till  the  required  level  is reached. First 2 layers of 15 to 20 cms shall be free from stones or chips or any harmful material, to protect the pipe from damage.

Only soil or soft murum shall be used for filling.

Originally filling shall be done 30 to 40 cms above natural ground or road level. Sinking below the road or ground level, if noticed till the completion of work, the contractor shall have to make it level at his cost.

This item includes,

- Clearing useful excavated material of rubbish bricking clods, stone, etc.

- Conveying the useful excavated material up to 500 M and filling in layers, watering and compacting.

- All labour, equipment and other arrangements necessary for the satisfactory completion and completion of the item.

## Mode of measurement and payment

The  rate  shall  be  for  a  unit  of  1  cum  of  compacted  trench  filling  with  approved excavated  material. The measurement  shall  be  net  for the  compacted filing  and no deduction for shrinkage or voids shall be made. However, deduction for pipe volume will be made. Depth of filling for measurement will be limited from natural ground level only. No payment will be made for filling for 30 to 40 cms above natural ground level, if so insisted by the Engineer-in-charge.

Surplus excavated material is the property of Pradhikaran. So contractor is not empowered to sell this excavated material to any other agency.

This disposal will not be considered for initial 500 M lead from edge of pipe line trenches and so will not be paid for.

The material shall be conveyed by means of suitable devices/manner.

The material conveyed to the place of disposal shall either be stocked or spread as directed by Engineer-in-charge or his representative.

The route opening and maintenance, payment of any royalties, compensation to land owners and for damaged of any etc. during the process of conveyance etc. shall be the entire responsibility of the contractor.

90 % payment made after completion of lowering, laying and remaining 10% amount will be withheld till satisfactory hydraulic testing of pipe line is given.

Thrust Block

The thrust block for foundation NRV/SV using M-200 concrete shall be provided. All foundations shall be made finished with proper edges and surfaces.

Supporting of pipe work and valves by means of reinforced cement concrete thrust block shall be in scope of bidder. Contractor shall construct all thrust block, foundation and piping encasing work during the installation. Or at the time of construction of the pump house and sump. Bidder shall have to provide the drawing and base frame for the preparation of the foundation. Bidder shall have to provide udder pipes and flanges at site of work during the construction of vertical retaining walls of sump and pump house & inserting the pipe through RCC/Brick walls with water proof sealing.

The thrust block to common manifold free end / bend should be designed and got approved from the Dept. Proper RCC chairs blocks should be provided to common manifold.

# Crossing Railway, Road and Canal

At, and Road , Railway ,& canal crossings the work shall be performed to the specifications Of local authorities or such public bodies as may be in charge (S) of Roads, Railway and Canals to be crossed. In case, however the minimum requirements of the governing agencies are less than Those set out in the drawing or the specifications given herein, then the Requirements given in the drawings and the Specifications given for encased line Shall be followed. Whereas the casing pipe in the case of encased line to be laid normal by boring, tunneling, engineer-in-charge may at his discretion permit open-cuts to be made for the installation of casing provided, however, that the TENDERER shall procure the necessary permit / license for the same from competent authority.

At locations wherein the open cut methods are permitted, the TENDERER shall pass the carrier pipe through the casing located in the trench after the approval of the engineer in charge in writing and care shall be exercised to avoid damage to pipe coating and wrapping during this operation. The TENDERER shall produce a certificate in writing from concerned authorities for its satisfactory restoration and payment therefore. At all crossings the carrier pipe shall be laid straight without bends so that if Necessary the pipe at a later date may be replaced without cutting the casing.

The Carried pipe shall extend at least 2 meters beyond the end of casing pipe at either End. At Road crossings the TENDERER shall eliminate unnecessary bending of pipe to  Conform  to  the  contour  of  ground  by  gradually  deepening  the  ditch  at  such Approaches as directed by the engineer – in - charge. Where the installation of the Casing has been made by open cut TENDERER shall install suitable  Temporary bridge Work ensuring the safety of the traffic aids and safeguards for protection of the Public safety, or he shall provide suitable diversions as desired by the engineer in Charge.

At all Roads, Railway pipeline crossings shall be bored with horizontal boring machine. The method of carrying out a cased crossing by boring for various crossings on this Pipeline route shall be jointly inspected by the representative of the COMPANY and TENDERER for each category of work prior to commencement of actual work. Pipeline under Road track and irrigation canal an applicable portion of the right of way shall be encased in accordance with the specification. This item of work shall include, necessary clearing and grading required therefore, trenching to the depths and widths

required, welding of casing and carrier pipes, testing, lowering in, Installation of vent assembles, end seals, insulator and all other fittings that may be Required, backfilling, clean up, complete restoration to the original condition and Further strengthening and protective works as may be required.

The work shall be carried out in accordance with the drawings and as directed by the engineer-in-Charge. For various operations mentioned above, the specifications pertaining to these operations shall apply in addition to the specifications given herein. The TENDERER shall be permitted to use William Sons type Neoprene seals in place of concrete end seals for the crossings. The item shall be procured by the TENDERER Himself as per the provisions under the appropriate head of work in case TENDERER so desires.

# ROAD REINSTATEMENT

## Reinstatement of Surfaces

During the laying of pipeline work, the surfaces is likely to be encountered, broken up and restored in the course of pipe laying same as existing surface. The surfaces may be:-

- Concrete roads

- Bituminous roads

- WBM roads

Contractor has to make temporary reinstatement and then permanent reinstatement to match the same as existing surface. Contractor should take all care during the work. If through the improper use of excavating machinery or plant, or through carelessness, or for any other avoidable reason the Contractor excavates trenches to greater widths than those specified, or if in the remaining parts of roads, tracks or footpaths, damage is done to surfaces by crawler tracks or wheels of heavy machinery, the Contractor shall be entirely responsible for the complete Reinstatement of surfaces to the condition pertaining before the Contractor commenced his operations, or shall pay to the appropriate authority the certified cost of such repairs as directed by engineer in charge.

## Temporary Reinstatement

During pipe laying work, contractor will have to make temporary reinstatement for the completed course of pipe laying. The filling of the trench shall be taken up to a depth of 450mm from the finished surface.  From this level to within 125mm of the surface the filling shall be approved gravel or crushed stone of the following grading:

| Sieve Size | Percentage by Weight Passing |
| --- | --- |
| 75 mm | 100 |
| 37.5 mm | 85-100 |
| 10 mm | 45-100 |
| 5 mm | 25-85 |
| 600 µm | Aug-45 |
| 75 µm | 0-10 |

The material shall be placed in layers not exceeding 200 mm unconsolidated depths and shall be fully compacted to form a stable backfill. The top 125mm shall be road base.

The material according to relevant IS code of practice or as per MORTH specification. The surface shall be rolled with a vibrating roller.

The Contractor shall maintain a constant and careful vigilance over the temporary surfaces constructed by him and shall be responsible for their appearance and repair during three months settlement period. As and when depressions occur in the temporary Reinstatement these shall be promptly filled by the Contractor to a level flush with the adjacent surface and adequately sealed as directed by Engineer in charge.

## Permanent Reinstatement

- Concrete Roads

Existing concrete slabs shall be broken back at least 150mm beyond the edges of the excavation and their exposed faces shall be inclined between 10 and 30 degrees to the vertical.  The limit of breaking out shall be delineated by straight saw cuts not less than 25mm in depth.  Where the slab is reinforced the reinforcement shall be preserved so that it projects at least 150mm from the exposed face.     The permissible deviation of irregularities in the surface of the trench backfill shall be ± 15mm.  The level of backfill should be such that  the new concrete slab  is  50mm thicker than  the existing.   The exposed  edges  of  existing  concrete  shall  be  clean,  free  from  all  cracked  or  loose material, and shall be painted with freshly made cement grout immediately before the new concrete slab is placed.

Where excavation interferes with a joint in an existing slab, it shall be reinstated, as found, including any dowel bars, joint filler and sealing compound. Reinforcement which has been cut out shall be replaced with new reinforcement of mass not less than that removed, accurately cut and wired to existing reinforcement. For new course of CC roads, concrete shall be Grade M300.

## Other Roads

Exposed edges of the existing carriageway shall be cut vertically to a uniform line consistent with the width of the trench. The depth of cut shall be equal to the combined

thickness of wearing course and base course. The undisturbed road base should be exposed to a minimum width of 75mm.

The temporary reinstatement shall be removed to the level of the formation of the existing road and the surface shall be well compacted. The sub-base, road base and subsequent courses shall be laid and compacted in accordance with the provisions of IS code of practice or as per MORTH standards. Care shall be taken that the exposed edges of existing carriageways are treated with prime coats or tack coats, as appropriate, before laying of road base and subsequent courses

# PUMPS SPECIFICATIONS

## Vertical turbine pump (water lubricated) Essential Design Requirements

The Vertical Turbine Pump offered shall satisfy the following basic design features.

  - It shall have a rising head characteristic.

  - The impeller adjustment shall be such that, the impellers run free in any installed condition in spite of the extension of line shaft caused by hydraulic down thrust and weight of shafting and impellers.

  - It shall be designed for non-overloading of prime mover.

  - It shall be designed to run with closed sluice valve condition without overloading the prime mover.

  - The pumps shall run smooth without noise & vibration. The magnitude of peak to peak vibration at slip will be limited to 100 microns at the bearing housing.

Necessary NPSH curve shall be submitted and minimum submergence required shall be stated. The system head curve and performance curve for all level conditions is to be enclosed.

The pump shall be suitable for satisfactory operation at the duty conditions, the head range stipulated.

The pumps shall have following technical parameters and particulars.

- No. of pumps to be	… Nos

Installed	….. Working … stand by

- Discharge	LPS

- Duty head	mtrs.

- Working head range	……. mtrs. To	mtrs.

- Shut off head	Not less than	mtr.

- Pump efficiency at duty point	not less than 80 %

- Speed	1470 RPM

- Column pipe dia.	Not less than ……. mm

- Column pipe wall	Minimum …. mm thickness

- Column pipe flange	Minimum …. mm Thickness

- Pump/Line shaft material	Stainless steel AISI - 316

- Total column length	……. M. (Including bowl assembly)

- Strainer	Basket type, fabricated out of stainless steel bars

- No of Stages of Bowl	Not more than ….. Stages.

Assembly

- Column assembly & other	Stainless steel AISI 316 Fasteners

- M.S. Sole plate	Minimum …… mm

- Base frame Size.	Fabricated with ISMC …… mm

- Pump and column shaft	S.S. Not less than ….. mm

## V.T. PUMP SETS (Water Lubricated)

The Vertical Turbine pump sets shall be (self-water lubricated) suitable for following conditions and specifications.

  - The pump shall be of approved by the Superintending Engineer (M) and shall conform to IS: 1710 & shall satisfy test & trial as per IS: 5120 with latest modifications from time to time.

  - Pump efficiency shall not be less than 80% at duty point under all circumstances & shall be maintained for 3 years from date of commissioning of the pumps.

  - Constructional and design details of the set shall be as follows.

- Impeller

Impellers shall be Stainless Steel CF8M shall be statically and dynamically balanced. Balancing holes in impeller are not acceptable.

- Wearing Rings

It  shall  be  of  Bronze  conforming  to  IS:  318  and  suitable  Grade  and  shall  be  of renewable type. It shall be held in place against rotation by screw in or locking with pins press fitted locked with pins. The wearing rings shall be provided on both impeller and casing.

Composite design of line shaft material and diameter and bearing centres shall ensure that the entire rotating assembly is brought from stand still to full speed without any vibration, whipping and shaft deflection and to ensure that first critical speed is not within 75% to 125% of full speed.

- Column Pipe Assembly

Column pipe shall be of M.S. ERW Fabricated heavy duty flanged type.  Thickness of column pipe shall not be less than 6 mm.  Each length of column pipe shall be designed to  accommodate  guide  bearing  holders  and  in  Standard  length  of  1.5  Mtr.  and matching distance piece pipe required for the total length of ……. Mtr. column length. Spider shall be provided with nitrile rubber bushing.

- Suction Bell Mouth

Entrance dia of Bell mouth shall be such that the suction velocity shall not exceed 1.5 m/sec. and shall be of M.S. heavy duty/C.I. The shape and curvature of the bell mouth shall  be designed for streamlined flow  of bowl  suction,  the thickness of  bell  mouth shall not be less than 12 mm.

- Strainer

Suction strainer shall be of flanged type heavy duty made from S. S AISI 410 plate of thickness not less than 10 mm. Total area of perforations shall not be less than 300% of entrance area of bell mouth. Stainless steel hardware shall be provided.

- Bowl Assembly

The pump bowl / bowls shall be flanged type with machined matching of faces. The suction bell mouth, bowl assembly, column pipe and all Joints shall be of flange joints. The bowls shall be capable of withstanding a hydrostatic pressure equal to twice the duty-head or 1.5 times shutoff head whichever is greater.

- Discharge Head

Discharge head shall be fully flanged type fabricated from M.S. C.I. It shall incorporate full diameter radial branch (same as that of column pipe) stuffing box with renewable bushing and taping for pressure gauge.  It shall be of robust construction and shall be designed  to  support  HS  or  VSS  motor  &  entire  loading  of  pump  assembly,  water column etc. and shall with stand all static, dynamic, torsional loads hydraulic thrust imposed during operation from shutoff to stipulated operating conditions and thrust due to change in direction of flow without any vibration. The discharge head shall be capable of withstanding hydrostatic pressure equal to twice the duty head or 1.50 times shut off head whichever is greater. The discharge head shall be properly supported to eliminate vibration.  An air cock of 50 mm dia. with same size of ‘B’ class G.I. pipes, bend shall be fixed to the discharge head. The G.I. B Class pipes shall be suspended vertically in the well with adequate length to release air

- Sole Plates

M.S. Sole Plate of minimum 30 mm or above thickness machined from both the sides shall be provided. The size of sole plate shall cover entire pump supporting girders (base frame). Suitable opening shall be provided at the centre, considering diameter of bell mouth bowl assembly and strainer.

The  Sole  Plate  shall  be  fixed  with  nut  bolts  on  200  mm.  ISMC  frame  and  shall  be machined.  The sole plate shall be kept on girders and blue matched to the extent of least  60  %  of  contact  area.   If  necessary  uneven  surface  shall  be  smoothened  with polish paper / smooth file.   The sole plate shall be perfectly levelled with straight edge and precision level.  The sole plate shall have tapped holes to receive discharge head. The bottom and top of sole plate shall be blue matched to have at-least 60% contact area. Use of shims will not be permitted for pump levelling.

- The pump shall be driven by vertical hollow shaft Or Solid shaft motor and shall be provided with non-reversible ratchet, check nut, flexible coupling etc. Complete.

- Special tools i.e. two pairs of erection clamps for the column and line shaft as recommended by manufacturer, adjusting nut spanner & impeller collate hammer shall be supplied with each pump set.

- Pre Lubrication Tank & Other Accessories: - In order to lubricate line shaft bearing of the pump, lubrication arrangement comprising the following shall be provided.

- Lubrication tanks 2 Nos. interconnected with each other common for all pumps fabricated from M.S. sheet metal of thickness not less than 5 mm and of capacity not less than 1 m3. The tank shall be cylindrical and shall be installed on pump mounting floor with concrete saddles or as directed during execution by Engineer- in-charge.

- Each lubrication tank shall be equipped with the following:

  - W. L. side gauge

  - Over-flow lead to sump

  - Drain valve lead to sump

  - “B” Class G.I. pipe connection with isolating valve and non-return valve to each pump column assembly for lubrication. The valve shall be located near the tank. The size of individual pipe and valve to pump shall be 40 mm diameter.

  - Inlet connection with solenoid operated valve and suitable removable strainer by suitable tapping from common header.

  - Float valve in the tank for control of overflow.

  - Any other item necessarily required for proper functioning of water lubrication arrangement.

TESTING

All the pumps shall be subject to factory test in presence of Superintending Engineer

(M) or his representative and third party inspection agency approved by MJP.

## Factory test

- Hydrostatic Test

Following item shall be tested at hydrostatic pressure equal to twice duty head or 1.5 times shut off head of bowl assembly whichever is higher as per  IS : 5120.

Bowl assembly	-	Each. Discharge Head.	-	Each.

Column Pipes At least 20% of total quantity

- Performance Test

Performance  test  of  each  pump  should  be  carried  out.   The  test  shall  generally  be carried out as per IS: 10981 of acceptance test for pumps Class - B.  The test shall be carried out at full speed &  full load at manufacturers work. The test shall cover six points i.e.

- Duty point.

- Two points above duty point.

- Two points below duty point.

- Shutoff head

- Power consumption at all above points.

  - The test at reduced speed will not be accepted.

  - c)	Strip Inspection

Two pump sets out of five of pure water after completion of its performance test and as selected by the Engineer or inspector at random will be offered for strip-inspection and dimensional checking. The manufacturer/contractor shall submit all required dimensional drawings. Minimum points as under shall be checked.

  - Original dimensions of impeller, neck ring etc.

  - Condition of all components particularly bushes, bearing, and wearing rings to examine for undue rubbing, wear etc. and verification of dimensions after performance test.

  - Dynamic balancing of (a) Impeller, (b) Flexible coupling, shall be carried out as per relevant IS.

  - Verification of clearance and tolerance between :

- Wearing rings

- Impeller shaft and bearings

- Impeller shaft and key

- Shaft and flexible coupling

- Key and keyway on shaft at (d)

- Finish of water passage in impeller and diffuser.

- Review of raw Material Test Certificate and quality control procedure.

Any deviation from tenders specifications & related IS shall be pointed out in inspection report.

Material test certificate to the various pump components shall be furnished.

## Field Performance Test

Field test shall be witnessed by at least Two Engineers of MJP.

The test shall be carried out as per IS: 10981 Code of acceptance test of pump   Class- B, in general and stated below in particular. The purpose of field test is not to ensure whether pump performance as regards acceptance limit as per IS: 9137, the purpose is to  ensure  that  the  pump  performance  is  generally  acceptable  or  otherwise.    Final acceptance shall be as per following criteria.

- Verification of guarantee for H and Q specified in Clause 9.4.1 shall be based on following liberalised tolerances.

XHv	+ 0.006

XQv	+ 0.09

- As regards P-Q. Characteristics for acceptance. It shall be checked whether motor is not getting overloaded within specified head range.

## Volumetric

Volumetric measurement shall be taken on the basis of rise of level in clarifloculator. In addition, one Ultrasonic calibrated flow meter shall be arranged by the contractor at his cost

- The head shall be measured with calibrated pressure gauge of accuracy 1% or better. At least three pressure gauges shall be used dully calibrated from two different institutions with prior approval of the Engineer. The calibration shall be point to point and not mere for percentage error. The gauge shall be fitted at suitable place on the discharge nozzle. It may be noted that the stipulation that pressure gauge shall be installed at least two times diameter away from discharge nozzle and delivery valve be placed at least four times diameter away from discharge nozzle cannot be simulated at site conditioned no allowance for this deficiency shall be considered. The decision of Engineer in-Charge shall be final.

- The input power to motor shall be measured with 2 Nos. class 0.5 accuracy single phase watt meters with suitable CTs test lid and PTs provided in panel. The wattmeter, CTs and PTs shall be got calibrated from approved institutions. The calibration shall be for point to point and not mere for percentage error.

- The speed shall be measured by at least two numbers, non-contact tachometer with digital display and calibrated from two institutions, approved by the Engineer.

- The field test shall be taken with entire head range in such a manner that it would cover at least 6 points (i.e. duty point, 2 above, 2 below and shut off). The guarantees for head and discharge shall be deemed to be fulfilled as per clause under 9.4.1 of IS: 10981.

- The field performance test at site is absolutely essential as above (a) to (e).

Make: As per approved list of MJP.

## Centrifugal pump (pure water) Essential Design Requirements

The Centrifugal Pump offered shall satisfy the following basic design features.

  - It shall have a rising head characteristic.

  - It shall be designed for non-overloading of prime mover.

  - It shall be designed to run with closed sluice valve condition without overloading the prime mover.

  - The pumps shall run smooth without noise & vibration. The magnitude of peak to peak vibration at slip will be limited to 100 microns at the bearing housing.

Necessary NPSH curve shall be submitted and minimum submergence required shall be stated. The system head curve and performance curve for all level conditions is to be enclosed.

The pump shall be suitable for satisfactory operation at the duty conditions, the head range stipulated.

The pumps shall have following technical parameters and particulars.

- No. of pumps to be	… Nos

Installed	….. Working … stand by

- Discharge	LPS

- Duty head	mtrs.

- Working head range	……. mtrs. to mtrs.

- Shut off head	Not less than mtr.

- Pump efficiency at duty point	not less than 70 %

- Speed	1470 RPM

- No of Stages	Not more than stages.

- Base frame size.	Fabricated with ISMC …… mm

- Pump shaft	S.S. Not less than	mm

## Horizontal Centrifugal Pumps

Pump Performance

The pumps shall have preferably best efficiency point when operating at … m of head. The pumps shall have a stable characteristics within the operating head range +7% - 15%.

## Constructional Features of Centrifugal Pump

The pumps shall be single stage horizontally split casing, double suction centrifugal pumps. The casing shall be provided with tapping and bronze collared plugs for air release. The make of pump shall be approved make by the Executive Engineer.

The impeller shall be shrouded double suction type and shall be balanced both statically and dynamically. The interior surfaces and passages shall be smoothly finished.

The shafts shall be of solid type. The shaft sleeves shall be securely keyed to the shaft. The bearing shall be heavy duty, antifriction ball bearing.

The stuffing boxes shall be of such design as to enable repacking without removal of any part except gland and lantern ring. The lantern ring shall be axially split water lubricated type and shall be easily removable. The stuffing boxes shall be provided with a drain hole for connecting drain pipe to drain the leaked water through gland.

The pumps shall be provided with a common base plate of fabricated steel or cast iron for mounting of pump and motor. If base plate of fabricated steel is provided, it shall be sufficiently rigid and design shall be got approved prior to fabrication. The fabricated base plate shall not be acceptable if shims plate are required for alignment of pump and motor set.

The coupling between pump and motor shall be steel pin and rubber bush type flexible coupling of adequate size. The coupling shall be dynamically balanced after being keyed to the shaft.

The suction and delivery connections shall be integrally cast with the casing, the flanges being flat faces and drilled to IS: 1537.

Both suction and delivery ends of the casing shall be provided with a 12 mm (1/2") tapping for mounting of pressure gauges.  The tapings shall be provided with bronze

collared plugs.   Each pump shall be provided with 150 mm  dia pressure gauge and vacuum  gauge  with  S.S.  siphon  tube,  vibration  damper  and  S.S.  isolating  cock  and suitably calibrated to indicate pressure from 0 m to 100 m and vacuum of 0 to 760 mm of Hg.

All other accessories e.g. funnel, air vent etc. shall be provided.  Also necessary cement concrete foundation block in M-200 shall be provided and cast by the contractor without any extra cost for erection of each pump motor set.

## Material and Construction

Pump Casing	Grey cast iron conforming to Grade 20 of IS: 210.

Impeller	Bronze conforming to IS: 318 Grade-II

Shaft	CS. IS: 2073, Gr. C-40 or SS AISI 410

Shaft sleeve	Stainless steel S.S. AISI-410 OR C.I. IS: 210 Gr. FG-200

Wearing Rings	Bronze

Flexible coupling	Forged steel conforming to IS: 3445

## Testing and Inspection

- Mechanical and hydraulic shop tests on pumps

Each pump shall be factory tested for satisfactory mechanical and hydraulic operation at full load speed in presence of MJP authorities. The performance test shall be taken with entire head range in such a manner that it would cover at least five points on the head discharge curve (one at duty point and other above and below duty head). Three certified copies of test records for each pump shall be submitted to the Engineer immediately upon completion of the factory test.

## Field Test

The field test shall generally be carried out as per IS.  The volumetric measurements of discharge would be on the basis of depletion of levels in the sump from which water is   pumped.     Discharge   measurement   by   calibrated   ultrasonic   flow   meter   also acceptable. The effective head shall be measured with pressure gauge fitted to delivery pipe at an elevation of at least 2 m. above the delivery pipe.  The gauge shall be fitted at 1 m distance from the discharge nozzle.   The reading may be taken with different gauges.  The tenderer shall note that the stipulation of delivery valve be placed at at least 4 times the diameter away from the discharge nozzle cannot be simulated due to site conditions and no allowance for this deficiency shall be considered.  The electrical inputs will be measured with the help of calibrated energy meter.

The pumps showing a fall of efficiency below guaranteed efficiency while operating at duty point shall not be accepted unless necessary rectification is carried out by the Contractor to restrict the efficiency shortfall in field test up to the quoted efficiency.

## Testing

All the pumps shall be subject to factory test in presence of Executive Engineer (M)/Superintending Engineer (M) or his representative and third party inspection agency approved by MJP.

## Factory test

  - Hydrostatic Test

Following item shall be tested at hydrostatic pressure equal to twice duty head or 1.5 times shut off head whichever is higher as per  IS : 5120.

  - Performance Test

Performance  test  of  each  pump  should  be  carried  out.   The  test  shall  generally  be carried out as per IS: 10981 of acceptance test for pumps Class - B.  The test shall be carried out at full speed &  full load at manufacturers work. The test shall cover six points i.e.

- Duty point.

- Two points above duty point.

- Two points below duty point.

- Shutoff head

- Power consumption at all above points.

The test at reduced speed will not be accepted.

  - Original dimensions of impeller, neck ring etc.

  - Condition of all components particularly bushes, bearing, and wearing rings to examine for undue rubbing, wear etc. and verification of dimensions after performance test.

  - Dynamic balancing of (a) Impeller, (b) Flexible coupling, shall be carried out as per relevant IS.

  - Verification of clearance and tolerance between :

  - Wearing rings

  - Impeller shaft and bearings

  - Impeller shaft and key

  - Shaft and flexible coupling

  - Key and keyway on shaft at (d)

- Finish of water passage in impeller and casing.

- Review of raw Material Test Certificate and quality control procedure.

Any deviation from tenders specifications & related IS shall be pointed out in inspection report.

Material test certificate to the various pump components shall be furnished.

## Field Performance Test

Field test shall be witnessed by at least Two Engineers of MJP.

The test shall be carried out as per IS: 10981 Code of acceptance test of pump   Class- B,   in general and   stated below in particular. The purpose of field test is not to ensure whether pump performance as regards acceptance limit as per IS: 9137, the purpose is to  ensure  that  the  pump  performance  is  generally  acceptable  or  otherwise.    Final acceptance shall be as per following criteria.

  - Verification of guarantee for H and Q specified in Clause 9.4.1 shall be based on following liberalised tolerances.

XHv	+ 0.006

XQv	+ 0.09

  - As regards P-Q. Characteristics for acceptance. It shall be checked whether motor is not getting overloaded within specified head range.

- Volumetric

Volumetric measurement shall be taken on the basis of rise of level in clarifloculator. In addition, one Ultrasonic calibrated flow meter shall be arranged by the contractor at his cost

- The head shall be measured with calibrated pressure gauge of accuracy 1% or better. At least three pressure gauges shall be used dully calibrated from two different institutions with prior approval of the Engineer. The calibration shall be point to point and not mere for percentage error. The gauge shall be fitted at suitable place on the discharge nozzle. It may be noted that the stipulation that pressure gauge shall be installed at least two times diameter away from discharge nozzle and delivery valve be placed at least four times diameter away from discharge nozzle cannot be simulated at site conditioned no allowance for this deficiency shall be considered. The decision of Engineer in-Charge shall be final.

- The input power to motor shall be measured with 2 Nos. class 0.5 accuracy single phase watt meters with suitable CTs test lid and PTs provided in panel. The wattmeter, CTs and PTs shall be got calibrated from approved institutions. The calibration shall be for point to point and not mere for percentage error.

- The speed shall be measured by at least two numbers, non-contact tachometer with digital display and calibrated from two institutions, approved by the Engineer.

- The field test shall be taken with entire head range in such a manner that it would cover at least 6 points (i.e. duty point, 2 above, 2 below and shut off). The guarantees for head and discharge shall be deemed to be fulfilled as per clause under 9.4.1 of IS: 10981.

- The field performance test at site is absolutely essential as above (a) to (e).

## 415 V horizontal foot mounted MOTOR:-

The Motor should have following technical parameters and particulars.

KW of Motor	Minimum …… kW

Qty	2 Nos

Speed	1500 Rpm Synch.

Type	Horizontal foot mounted

Enclosure	TEFC - IP 23

Rated voltage	415 kV + 10 %

Frequency	50 Hz + 3 %

Phase	3 phase, AC

Insulation	B/F - Class

Duty	S-1

The  tenderer  shall  provide  415  V  totally  enclosed  fan  cooled  induction  motors  of approved make suitable for driving pure  water centrifugal  pumps  (Item No.1). The motors shall conform to IS: 325 the contractor shall have to supply winding data of motor duly signed by manufacturer.

The motor shall be suitable for voltage variations of + 10% and frequency variation of

+ 3% and combined variation of + 10%.

## Design

- The rated power of the motor shall be at least 20% above at duty point and at least 10% above the maximum power required over rated head range of pump.

- The starting time and locked rotor withstand time under hot condition shall have suitably discrimination for proper selection of protection relay. The locked rotor withstand time under hot conditions and at 110% rated voltage shall be more by at least three second than the starting time with driven equipment coupled and at 85% rated voltage.

The motor shall be suitable for restricted operation at following conditions.

- Accelerating the driven equipment from stand still to full speed within duration of one minute or less at 85% of rated voltage.

- Operation on load at 75% of rated voltage for 5 minutes.

- Two starts in quick succession from cold condition.

- One hot restart at maximum steady state temperature over ambient temperature of 48 Degree Centigrade

- Three starts per hour equally spaced over the duration after attaining thermal equilibrium.

The class of insulation of the motor shall be minimum 'B' class. However temperature rise of the motor when operating at extreme conditions of voltage and frequency variation shall not exceed 80 0C by thermometer and 90 oC by resistance over an ambient temperature of 45 oC at site.

## Construction

The motor shall be foot mounted TEFC induction type. The motor shall be statically and dynamically balanced and critical speed shall not be in the range of 80 % to 120 % of the motor speed.

The motor shall having heavy duty anti-friction bearing, grease lubricated type.

The cable box shall be phase segregated and with degree of protection conforming to IP 54. The terminal box shall be suitable for termination of power cables as per size

incable schedule. The fault withstand capacity of the cable box shall not less than the fault level specified in Section-1.

## Accessories

Shaft mounted cooling fan of cast iron/aluminum or mild steel and	dynamic balanced.

Test, vibration and noise

The   vibration   level   should   be   within   permissible   limit   (IS:   12075)   and   noise level shall be 80 db or less for which the certificate shall be submitted.  Manufacturer test certificate should be submitted by the contractor

# Compound Wall

General Precast reinforced cement concrete work should be directed by Engineer-in charge according to the nature of work.

## Precast Concrete

  - Concrete shall be casted according to relevant standard method as applicable code which is mentioned. Necessary care should be taken on plant/site during casting of unit.

  - The casting shall be done in required mould & formwork relevant size required. Proper vibration shall be needed as Table Molded vibration method.

  - Reinforcement shall be placed according to design and standard practice

  - Grade of Concrete must be M20 for Foundation work and M25 for wall casting work.

  - For Specification of R.C.C work shall be followed As per Schedule B-4 & B5.

  - Precast concrete shall comply with IS: 456 and with the following requirements: All precast units shall be cast on a suitable bed or platform with firm foundation and free from wind.

  - Contractor shall be responsible for the accuracy of the level or shape of the bed or platform. A suitable serial number and the date of casting shall be impressed or painted on each unit.

  - Striking forms Side shutters shall not be struck in less than 24 hours after depositing concrete and no precast unit shall be lifted until the concrete reaches a strength of at least twice the stress to which the concrete may be subjected to at the time of lifting.

## Precast units

The lifting and removal of precast units shall be undertaken without causing shock, vibration or undue bending. Contractor shall satisfy Engineer or his representative that the methods proposed to adopt for these operations will not over-stress or otherwise effect seriously the strength of the precast units. The reinforced side of the units shall be distinctly marked.

## Curing

All precast work shall be protected from the direct rays of the sun for at least 7 days after casting and during that period each unit shall be kept constantly watered or preferably be completely immersed in water if the size of the unit so permits. Otherwise curing practice as given in Clause 9.6.9 shall be followed.

Precast  concrete  solid  units  shall  be  measured  separately  and  shall  include  use  of moulds, finishing the top surface even and smooth wooden trowel, before setting in position in cement mortar 1:2 (1cement : 2 coarse sand)

CHAPTER : V

DRAWINGS